GAS PROCESSING & METHANOL COMPLEX PROJECT NO. BFPCL-DSV-RAEC 2026

| Project | FEED for Gas Gathering Pipelines & Associated Infrastructure |
| --- | --- |
| Client | Brass Fertilizer and Petrochemical Company Limited |
| Originating Company | Epic Atlantic Limited |
| Document Title | Pipeline Decommissioning & Abandonment Philosophy |
| Document Number | EA-BFPCL-GGPL-FEED-GEN-PHY-006 |
| Document Revision | R01 |
| Document Status | Issued For Review |
| Coordinator | Aloy Duru |
| Security Classification | Restricted |
| Issue Date | 09 May 2026 |

Pipeline Decommissioning & Abandonment Philosophy

| R01 | 09 May 2026 | Issued for Client Review | Aloy O Duru | Obima Oragwu | Aloy O Duru |  |
| --- | --- | --- | --- | --- | --- | --- |
| Rev # | Issue Date | Status Description | Originator | Reviewed | Endorsement (Epic Atlantic) | Approval (BFPCL) |

Revision History

| Rev. No. | Date | Description of Revision |
| --- | --- | --- |
| P0 | 28 Apr 2026 | For Review |
|  | 04 May 2026 | Incorporating Metering Systems previously omitted, and General Update |

Revision Philosophy:

- All documents for review shall be issued at R01, with subsequent R02, R03, etc as required.

- All documents approved for issue or approved for design shall be issued at A01 with subsequent A02, A03, etc. as required. (Management of Change is required for A02, A03, etc.)

for the subsequent project phases, post FEED, it is expected that:

- All Detailed Design documents for review shall be issued at D01, with subsequent D02, D03, etc. as required.

- All documents approved for construction shall be issued at C01 with subsequent C02, C03, etc. as required. (Management of Change is required for C02, C03, etc.)

- All approved “As-Built” documents shall be issued at Z01, with subsequent Z02, Z03, etc as required. (Use versions Z01.1, Z01.2, Z01.3, etc to review the “As-Built” document to Z02).

Restricted

This document is made available subject to the condition that the recipient will neither use nor disclose the contents except as agreed in writing with the copyright owner.  Copyright is vested in Brass Fertilizer and Petrochemical Company Limited (BFPCL) © All rights reserved.

Neither the whole nor any part of this document may be reproduced or distributed in any form or by any means (electronic, mechanical, reprographic, recording, or otherwise) without the prior written consent of the copyright owner.

Summary Page

| Client: | Brass Fertilizer & Petrochemical Company Limited |  |
| --- | --- | --- |
| Project: | Gas Processing & Methanol Complex | Project No. BFPCL-DSV-RAEC 2026 |
| Facility: | Gas Gathering Pipelines & Associated Infrastructure | Doc No. EA-BFPCL-DSV-GGPL-FEED-GEN-PHY-006_R01 |

The administration of this document is limited to defining the philosophy and BFPCL/DSV commitment to the Decommissioning and Abandonment (D&A) of the entire 125 km OKNU–BBOU–ELEP–AKAB Gas Gathering Pipeline System and associated infrastructure for the BFPCL Gas Hub / Methanol Plant Project at the end of the asset’s operational life. The pipeline system comprises two interconnected segments: the 85 km OKNU–BBOU upstream pipeline segment, which operates under an independent Gas Sale and Purchase Agreement (GSPA) and maintains a distinct project status; and the 40 km BBOU–ELEP–AKAB downstream pipeline segment, into which the upstream segment injects gas for onward transportation to the BFPCL Gas Hub / Gas Processing Plant (GPP). Although both segments are technically integrated and are expected to undergo decommissioning and abandonment in a broadly similar manner at the end of their service life, they may be structured and executed separately to accommodate independent funding allocations, stakeholder responsibilities, commercial arrangements, and regulatory approval requirements. In addition, there remains a long-term strategic aspiration to transport up to 1 BSCFD of gas through the integrated pipeline network to a proposed 1 BSCFD gas hub at Akabel under a separate future development. However, the final configuration, commercial structure, and implementation philosophy of that future expansion remain subject to further definition and subsequent project development decisions. This document establishes the overarching principles, objectives, and general requirements governing D&A activities, in alignment with prevailing regulatory obligations and recognized industry standards, including those of the Nigerian Upstream Petroleum Regulatory Commission (NUPRC), the Nigerian Midstream and Downstream Petroleum Regulatory Authority (NMDPRA), the Federal Ministry of Environment (FMEnv), and the Environmental Guidelines and Standards for the Petroleum Industry in Nigeria (EGASPIN). While this philosophy document provides the intended framework for the anticipated D&A approach, the eventual execution strategy at the time of decommissioning shall remain adaptable to evolving regulatory requirements, technological advancements, environmental considerations, field conditions, stakeholder expectations, and emerging industry best practices applicable at that time. This report has been prepared using data, assumptions, and reference documents provided by the Client. Should additional information become available during subsequent phases of the project, Epic Atlantic reserves the right to review, amend, or update the opinions, recommendations, assumptions, and conclusions contained herein. For completeness and proper interpretation, this document should be read in conjunction with the referenced FEED documents and associated revisions listed herein, which collectively form integral components of the overall project basis and D&A philosophy.

KEYWORDS: BASIS OF DESIGN, PIPELINE, MANIFOLD, PLATFORM, MULTIPHASE FLOW, ROW, PTS

| REferences |  |
| --- | --- |
| Document No. | Description |
| TBA | Basis of Design Update |
| TBA | Design and Operating Philosophy Update |
| TBA | Upstream Gas Gathering Concept Select & Revalidation Report Update |
| FISAS Draft Report, Nov 2020 | ESIA Assessment BBOU-ELEP-AKAB 40 km Gas Supply Project |
| EA-BFPCL-DSV 0KNU-BBOU-ELEP-AKAB GGPL-FEED-CSM-001 | FEED Scope Definition of OKNU-BBOU-ELEP-AKAB Pipeline |
| Sckope Draft Report, TBA | Topographical, Geotechnical, and EIA Surveys of OKNU-BBOU, and Updates of BBOU-ELEP-AKAB Pipeline Route Survey |
| TBA | Relevant As- Built Drawings |

Table of Contents

Project Information, Terms, Abbreviations, and Definitions	7

Project Information – General	7

Definition of Terms	8

Abbreviations	9

1.	Executive Summary	11

1.1.	System Overview	11

1.2.	BFPCL / DSV Commitment	12

1.2.1.	Value Drivers	12

1.2.2.	Strategic Intent	12

1.2.3.	Governance & Regulatory Framework	12

1.2.4.	Execution Framework	13

1.2.5.	Key Risks & Mitigations	13

1.3.	The Decommissioning & Abandonment Process	13

1.3.1.	Pipeline Network	14

1.4.	Scope Of Decommissioning	14

1.4.1.	Pipelines	14

1.4.2.	Facilities & Process Systems	14

1.4.3.	Metering Systems (Custody Transfer & Verification)	15

1.4.4.	Check Meters (All Manifolds)	15

1.4.5.	Fiscal Meter (Final Custody Transfer)	16

1.5.	Schedule	16

1.6.	Cost Estimate (USD)	17

2.	Introduction & Background	18

2.1.	Base Case Gas Gathering System	18

2.2.	Gas Processing Plant (GPP) – 500 MMscfd	19

2.3.	Methanol Production Plant	19

2.4.	Floating LNG (FLNG) Facility/Fertilizer (Urea)	19

2.5.	Product Export System	19

2.6.	Produced Water Management	19

2.7.	Utilities and Offsite Infrastructure	19

2.8.	Pipeline Design Philosophy – Flexibility & Expandability	20

3.	Battery Limit, and Scope of Work	21

3.1.	Battery Limit	21

3.1.1.	OKNU Platform	21

3.1.2.	BBOU Platform	22

3.1.3.	ELEP Platform	22

3.1.4.	Akabel Facility	22

3.2.	Data Room Index Structure	22

3.2.1.	Project Overview	22

3.2.2.	Route & Survey	22

3.2.3.	Pipeline Engineering	22

3.2.4.	Facilities	22

3.2.5.	Crossings	23

3.2.6.	Mechanical & Materials	23

3.2.7.	Process & Instrumentation	23

3.2.8.	Electrical & CP	23

3.2.9.	Civil & Structural	23

3.2.10.	Testing & Commissioning	23

3.2.11.	Environmental	23

3.2.12.	Modifications	23

3.2.13.	Decommissioning (To Be Developed)	24

3.3.	Layout & Configuration	24

3.3.1.	Route & Alignment	24

3.3.2.	Crossings & Special Sections	24

3.3.3.	Mechanical & Materials	24

3.3.4.	Valves & Facilities	24

3.3.5.	Process & Control	25

3.3.6.	Electrical & CP	25

3.3.7.	Civil & Structural	25

3.3.8.	Testing & Commissioning	25

3.3.9.	Environmental	25

3.3.10.	Modifications & Deviations	25

3.4.	Submission Requirements	25

3.5.	KP-by-KP Drawing Relevance (OKNU → AKAB)	25

3.5.1.	KP 0 – KP 10 (OKNU → River Niger Crossing)	26

3.5.2.	KP 10 – River Niger Crossing	26

3.5.3.	KP 10 – KP 38 (Swamp Section)	26

3.5.4.	KP 38 – Midline Manifold (SEIB Tie-in)	26

3.5.5.	KP 38 – KP 66	26

3.5.6.	KP 66 – Midline Manifold (NUNR/DBUC Tie-in)	27

3.5.7.	KP 66 – KP 85 (BBOU)	27

3.5.8.	KP 85 – BBOU Manifold	27

3.5.9.	KP 85 – KP 93 (BBOU → ELEP)	27

3.5.10.	KP 93 – KP 125 (ELEP → AKAB)	27

3.5.11.	KP 125 – AKAB Gas Hub	28

4.	The Decommissioning & Abandonment Scope	29

4.1.	Governance	29

4.1.1.	Primary Regulators	29

4.1.2.	Core Legal Frameworks	29

4.1.3.	Technical & Operational Requirements	29

4.1.4.	Key Challenges in the Nigerian Context	30

4.1.5.	Ancillary Systems	30

4.2.	Decommissioning Philosophy	30

4.3.	Key Decommissioning Processes	30

4.3.1.	Planning & Approvals	30

4.3.2.	Shutdown & Isolation	31

4.3.3.	Cleaning & Hydrocarbon Removal	31

4.3.4.	Flushing, Drying & Inerting	31

4.3.5.	Metering Close-Out (Critical Step)	31

4.3.6.	Disconnection & Segmentation	31

4.3.7.	Execution (Removal / Abandonment)	31

4.3.8.	Waste Management	31

4.3.9.	Site Restoration	31

4.4.	Abandonment Activities	32

4.5.	KP-Based Execution Strategy	32

4.6.	Risk Management	32

4.7.	Conclusion	33

5.	Key Decommissioning Processes & Abandonment Activities	34

5.1.	Decommissioning Processes (End-to-End Execution)	34

5.1.1.	Pre-Decommissioning Planning	34

5.1.2.	System Shutdown & Isolation	34

5.1.3.	Pipeline Cleaning & Hydrocarbon Removal	34

5.1.4.	Flushing, Drying & Inerting	34

5.1.5.	Disconnection & Mechanical Works	34

5.1.6.	Pipeline Removal (Where Applicable)	35

5.1.7.	Waste Management	35

5.1.8.	Site Restoration	35

5.2.	Abandonment Activities (Pipeline Left In Place)	35

5.2.1.	Cleaning to Acceptable Standard	35

5.2.2.	Isolation & Disconnection	35

5.2.3.	Filling / Stabilization	36

5.2.4.	Cathodic Protection Decommissioning	36

5.2.5.	Long-Term Integrity Assurance	36

5.2.6.	Marking & Records	36

5.3.	Special Considerations for OKNU–BBOU–ELEP–AKAB	36

6.	Facilities Engineering Design Features	38

6.1.	Pipeline Routing Philosophy	38

6.2.	Liquid Management Strategy	38

6.2.1.	Upstream Liquid Removal	38

6.2.2.	Diameter Optimization	38

6.3.	Receiving Facility Protection	39

6.4.	Liquid Handling and Disposal	39

6.5.	Pipeline Capacity and System Integration	39

6.6.	System Integration	39

6.7.	Pipeline Routing and Terrain	40

6.8.	Pipeline Size Decision	40

6.9.	Metering System	41

6.9.1.	Wet Gas Metering (For Hydrocarbon Accounting)	41

6.9.2.	The Fiscal Metering system	41

6.9.3.	Other Metering Systems	41

6.9.4.	Governance & Integration	42

# Project Information, Terms, Abbreviations, and Definitions

## Project Information – General

| Project Information – General |  |  |
| --- | --- | --- |
| 1.0 | Employer | BRASS FERTILIZER & PETROCHEMICAL COMPANY LIMITED (BFPCL) |
| 2.0 | PMC | TATA CONSULTING ENGINEERS LIMITED (TCE) |
| 3.0 | EPCC (CONTRACTOR) | ENPPI/PETROJET/ENERFLEX CONSORTIUM |
| 4.0 | Project Title | Gas Processing and Methanol Complex |
| 5.0 | Location | Akabel, Brass Island. The project site is about 85 km South West of Port Harcourt, 70 km South of Yenagoa and 90 km West of Bonny Island. |
| 5.1 | State | Bayelsa State, Nigeria |
| 5.2 | Nearest Air Port and distance | Port Harcourt Airport (PHC), 80 km Yenagoa Airport (BIA), 75 km |
| 5.3 | Nearest Port | Port Harcourt (Onne) |
| 5.4 | Nearest Railway Station & distance | - |
| 5.5 | Highway and distance | Connected through water way only. Road connection does not exist. |
| 5.6 | Important Town and distance | Yenagoa, Nigeria& 67 km |
| 5.7 | Altitude Above Mean Sea Level | 9 m |
| 5.8 | Atmospheric pressure |  |
|  | Average | 1,013 mbar |
| 6.0 | Ambient Air Temperatures | (Refer Note-5,6) |
| 6.1 | Maximum | 38°C |
| 6.2 | Minimum | 18°C |
| 6.3 | Average | 23°C |
| 6.4 | Summer Design Wet Bulb Temp | 28°C |
| 6.5 | Winter Design Wet Bulb Temp | 15°C |
| 6.6 | MDMT | 15°C |
| 6.7 | Swamp temperature | 25°C (23°C to be used wherever a margin is required) |
| 6.8 | Ground temperature | 25 - 27.5 °C |
| 6.9 | Black-bulb temperature: | 80°C |
| 7.0 | Relative Humidity |  |
| 7.1 | Maximum | 95 % |
| 7.2 | Minimum | 51 % |
| 7.3 | Average | 73 % |
| 8.0 | Rainfall Data |  |
| 8.1 | Average annual rainfall | 3,800 mm |
| 8.2 | Max daily rainfall: | 180 mm |
| 8.3 | Mean max. Hourly rainfall | 100 mm |
| 9.0 | Transport |  |
| 9.1 | Name of the highway near which the plant is located | Connected through water way only. Road connection does not exist. |
| 9.2 | Access road | - |
| 9.3 | Railway (Gauge) | - |
| 10.0 | Wind Data |  |
| 10.1 | Design Wind Velocity | 35.6 m/sec (Note-1) |
| 10.2 | Wind Direction | Note-2 |
| 11.0 | Seismic Data |  |
| 11.1 | Earthquake Zone | Note-3 |
| 12.0 | High Flood Level (HFL) | * |
| 13.0 | Natural Ground Level | * |
| 14.0 | Slope | * |
| 15.0 | Drainage | * |
| 16.0 | Design temperature for Electrical equipment | 40°C |

## Definition of Terms

| TERMS | DEFINITIONS |
| --- | --- |
| BFPCL | Brass Fertilizer & Petrochemical Limited. |
| RENAISSANCE | Renaissance Africa Energy Company Limited |
| Employer | Party (Usually BFPCL) that initiates the project and ultimately pays for its design and construction. The Employer will generally specify the technical requirements. The Employer may also include an agent or consultant authorized to act for and on behalf of, the Employer. |
| Engineer | The party that carries out the FEED Engineering of the project. |
| Manufacturer/Supplier | Party, which manufactures or supplies equipment and services to perform the duties specified by the Contractor. |
| Shall | The word ‘shall’ indicate a mandatory requirement. |
| Should | The word ‘should’ indicate a recommendation. |
| Measuring Range | Range defined by LRL and URL within which the limits of uncertainty of the measuring instrument are specified (the capability of the instrument). |
| On-Line Instruments | Instruments connected to process and utility lines or equipment via primary isolation valves. |
| Project | Front End Engineering Design for Gas Gathering Pipelines (Phase1) |

## Abbreviations

| Abbreviation | Meaning |
| --- | --- |
| AASHTO | American Association of state Highway Transportation Officials |
| AGEF | Above Ground End Facilities |
| ALARP | As Low as Reasonably Practicable |
| API | American Petroleum Institute |
| ASTM | American Society of Testing and Materials |
| BOD | Basis Of Design |
| CP | Cathodic Protection |
| CPT | Cone Penetrometer Test |
| CTMS | Custody Transfer Metering Station |
| DB&B | Double Block and Bleed |
| DCQ | Daily Contractual Quantity |
| DEP | Design and Engineering Practice |
| ESD | Emergency Shutdown |
| ESDV | Emergency Shutdown Valve |
| FEED | Front End Engineering Design |
| FGS | Fire, Gas and Smoke detection systems |
| GPP | Gas Processing Plant |
| GTG | Gas Turbine Generators |
| HAZID | Hazard Identification |
| HAZOP | Hazard Operability |
| HEMP | Hazards and Effects Management Process |
| HFE | Human Factors Engineering |
| HPU | Hydraulic Power Unit |
| HRA | Health Risk Assessment |
| HSES | Health, Safety, Environment and Security |
| HSSE & SP | Health, Safety, Security, Environment and Social Performance |
| IEC | International Electro-technical Commission |
| ISPM | Industry Standard Process Modules |
| JV | Joint-Venture |
| LCD | Liquid Crystal Display |
| LOI | Local Operator Interface |
| LRL | Lower Range Limit |
| LRV | Lower Range Value |
| LIRA | Logistics and Infrastructure Resource Assessment |
| MAC | Main Automation Contractor |
| NAG | Non-Associated Gas |
| OPC | OLE for Process Control |
| OPPS | Overpressure Protection System |
| PCD | Process Control Domain |
| PDMS | Plant Design and Management System |
| PEPF | Package Engineering, Procurement, and Fabrication |
| PIG | Pipeline Inspection Gauge |
| PVC | Polyvinyl Chloride |
| RTR | Reliability Test Run |
| SCE | Safety critical elements |
| SI | International System Units |
| SIL | Safety Integrity Level |
| SRB | Sulphate Reducing Bacteria |
| SIS | Safety Instrumented System |
| SWB | Steel Wire Braiding |
| URV | Upper Range Value |
| USC | US Customary Units |
| XLPE | Cross Linked Polyethylene |
| TEG | Tri-ethylene Glycol |
| TQ | Top Quartile |

# Executive Summary

This proposal defines the strategy and execution plan for the safe decommissioning and abandonment of the integrated OKNU–BBOU–ELEP–AKAB gas pipeline network, traversing the swamp and riverine terrain of the Niger Delta.

The approach adopts a hybrid strategy (Removal + Abandonment-in-Place) to:

Ensure zero residual hydrocarbon risk

Minimize environmental disturbance

Optimize cost and execution feasibility

Enable asset recovery (TAR)

The proposal is aligned with project FEED philosophy and regulatory expectations.

## System Overview

## BFPCL / DSV Commitment

This proposal sets out a regulator-aligned strategy and reaffirms BFPCL’s commitment to the safe decommissioning and abandonment of the 125 km OKNU–BBOU–ELEP–AKAB gas pipeline network in the Niger Delta. The approach adopts a hybrid methodology—combining Removal and Abandonment-in-Place—to achieve an optimal balance of:

- Safety risk reduction

- Environmental protection

- Cost efficiency

- Asset recovery value

### Value Drivers

- Eliminate residual hydrocarbon risk

- Minimize environmental disturbance (swamp/riverine sensitive zones)

- Optimize lifecycle cost and execution efficiency

- Preserve recoverable asset value

### Strategic Intent

Hybrid decommissioning approach (Removal + Abandonment-in-Place) delivering safe, compliant, and cost-effective pipeline retirement aligned with FEED philosophy and Niger Delta operating realities.

### Governance & Regulatory Framework

- Oversight by NUPRC (upstream) and NMDPRA (midstream/downstream) under the PIA

- Compliance with 2023/2024 Decommissioning & Abandonment Regulations

- Strong host community engagement and satisfaction requirements

- Mandatory Decommissioning & Abandonment Fund (escrow-backed financial assurance) as outlined below:

| s/n | Feature | Upstream (NUPRC) | Midstream NMDPRA |
| --- | --- | --- | --- |
| 01 | Primary Law | PIA 2021, Sec 232-233 | PIA 2021, Sec 111 & 232 |
| 02 | Fund Requirement | Bank Escrow (Annual) | Bank Escrow (Annual) |
| 03 | Environmental Standard | EGASPIN | NMDPRA Safety Regulations 2023 |
| 04 | Offshore Rule | IMO Standards (Full removal) | IMO Standards (Full removal) |
| 05 | Reporting | 36 months before cessation | Varies by license type |

### Execution Framework

- Early regulatory notification (3–36, depending on scope); and for this scope 12-36 months

      - Advance Notification: 12–36 months (system-wide) | ≥3 months (segment-level)

      - Planning Basis: 24 months to accommodate regulatory, environmental, and stakeholder approvals

- Comparative assessment

      - Total Removal vs. Abandonment-in-Place

- Pipeline hydrocarbon cleaning & purging to EGASPIN standards

- Pipeline sealing, isolation, and stabilization

- Post-abandonment monitoring and RoW integrity management

### Key Risks & Mitigations

- Host community acceptance → proactive engagement & Host Community Development Trust (HCDT) alignment

- Vandalism / illegal tapping → grouting, secure isolation, surveillance

- Divestment exposure → strict D&A fund adequacy and operator capability checks

## The Decommissioning & Abandonment Process

The decommissioning and abandonment of the 125 km OKNU–BBOU–ELEP–AKAB gas pipeline, at the end of its 30-year service life, will be executed through a safe, risk-based, and environmentally responsible hybrid strategy (Selective Removal and Abandonment-in-Place), tailored to terrain sensitivity and pipeline condition across swamp, riverine, and community areas, comprising:

- System isolation and depressurization, followed by hydrocarbon removal, cleaning, and inerting

- Integrity and environmental assessments to define segment-specific abandonment approaches

- Selective dismantling and recovery of above-ground facilities, crossings, and high-risk sections

- Abandonment-in-place of stable buried segments, with appropriate stabilization and route marking

- Compliance with Nigerian regulatory requirements (NUPRC/NMDPRA, FMEnv, EGASPIN) and international best practices

- Strong HSSE management, stakeholder and host community engagement, and responsible waste handling with emphasis on reuse/recycling

- Top of Form

- Bottom of Form

### Pipeline Network

- Total Length: ~125 km

- OKNU–BBOU: ~85 km (new line)

- BBOU–ELEP: ~8 km

- ELEP–AKAB: ~32 km

Key Nodes

- OKNU Manifold (KP0)

- River Niger Crossing (~KP10)

- Midline Manifolds (KP38, KP66)

- BBOU (KP85)

- ELEP (KP93)

- AKAB Gas Hub (KP125)

Terrain

- Predominantly swamp and mangrove

- Multiple river and creek crossings

- Offshore export interface

## Scope Of Decommissioning

The scope covers pipelines, facilities, instrumentation, and ancillary systems across the full 125 km corridor.

### Pipelines

- OKNU–BBOU pipeline (~85 km)

- BBOU–ELEP pipeline (~8 km)

- ELEP–AKAB trunkline (~32 km)

- Associated tie-ins and interconnections

### Facilities & Process Systems

- Inlet manifold (OKNU)

- Midline manifolds (KP38, KP66)

- BBOU and ELEP manifolds

- AKAB gas processing hub interface

- Slug catchers (inlet / midline / outlet)

- Pigging facilities (launchers/receivers)

### Metering Systems (Custody Transfer & Verification)

The pipeline network incorporates metering facilities at all manifolds and the gas plant outlet, forming a critical component of the decommissioning scope.

Wet Gas Meters (All Manifolds)

Installed at:

- OKNU (KP0)

- KP38

- KP66

- BBOU (KP85)

- ELEP (KP93)

- AKAB Slug Catcher Inlet

- AKAB Gas Plant Inlet

Function:

- Measurement of wet gas streams (with entrained liquids)

- Flow monitoring and allocation

Decommissioning Scope:

- Isolation and depressurization

- Removal of metering skids and instrumentation

- Preservation for reuse (subject to integrity verification)

### Check Meters (All Manifolds)

Installed at:

- OKNU (KP0)

- KP38

- KP66

- BBOU (KP85)

- ELEP (KP93)

- AKAB Slug Catcher Inlet

Function:

- Independent flow verification

- System balancing and reconciliation

Decommissioning Scope:

- Controlled shutdown

- Removal of meter runs and associated instrumentation

- Data archiving for audit purposes

### Fiscal Meter (Final Custody Transfer)

Installed at:

- AKAB Gas Plant Outlet (KP125)

Function:

- Revenue-grade custody transfer measurement

- Final export gas accounting

Decommissioning Scope:

- Controlled shutdown under monitored conditions

- Final calibration validation and reconciliation

- Removal, preservation, or re-certification

The strategy adopts a hybrid approach (Removal + Abandonment-in-Place) to:

- Eliminate residual hydrocarbon risk

- Minimize environmental disturbance

- Optimize lifecycle cost

- Preserve recoverable asset value

The approach is aligned with FEED philosophy, regulatory expectations, and Niger Delta execution realities.

## Indicative Combined D&A Schedule

| Phase | Activity | Indicative Duration |
| --- | --- | --- |
| 1 | Regulatory notification and stakeholder engagement | 4 months |
| 2 | Integrated engineering and D&A planning | 6 months |
| 3 | Environmental and statutory approvals | 4 months |
| 4 | Pipeline isolation, depressurization, and cleaning | 4 months |
| 5 | Removal of above-ground facilities | 5 months |
| 6 | Pipeline abandonment/removal activities | 9 months |
| 7 | River crossing stabilization and remediation | 4 months |
| 8 | Waste management and disposal | 4 months |
| 9 | Environmental remediation and restoration | 6 months |
| 10 | Final inspection, certification, and project close-out | 3 months |

Total Indicative Project Duration

Approximately 24–32 months, depending on seasonal access limitations, marine spread availability, regulatory approval timelines, contractor productivity, and stakeholder coordination requirements.

## Preliminary Combined USD Cost Estimate

| Item | Description | Estimated Cost (USD Million) |
| --- | --- | --- |
| 1 | Integrated engineering studies and D&A planning | 2.40 |
| 2 | Regulatory compliance and permitting | 1.20 |
| 3 | Pipeline cleaning, gauging, and flushing | 5.60 |
| 4 | Isolation and depressurization works | 1.70 |
| 5 | Removal of above-ground facilities | 6.80 |
| 6 | Selective pipeline removal works | 12.80 |
| 7 | Abandonment-in-place activities | 5.90 |
| 8 | River crossing remediation and stabilization | 3.40 |
| 9 | Waste handling, transportation, and disposal | 3.20 |
| 10 | Environmental remediation and restoration | 7.80 |
| 11 | Marine/swamp logistics and access support | 5.20 |
| 12 | Project management and supervision | 3.00 |
| 13 | HSE management and security support | 2.20 |
| 14 | Contingency allowance (15%) | 8.00 |

Total Preliminary Combined D&A Cost Estimate

USD 69.20 Million

The combined execution strategy indicates potential overall cost optimization when compared with the independent execution of both pipeline segments separately; mainly due to:

- Shared engineering and project management resources

- Single marine/swamp mobilization campaign

- Consolidated contractor and equipment utilization

- Integrated waste management and disposal logistics

- Reduced duplication of regulatory and stakeholder engagement activities

- Combined environmental remediation execution strategy

## Cost Estimate (USD)

# Introduction & Background

## Base Case Gas Gathering System

Network of pipelines and manifolds transporting gas from OKNU, BBOU, and ELEP fields to the central processing facility.

Schematics of Gas Supply from Okpokunou alongside Phase-1 Gas Supply

Satellite Imagery of Gas Supply from Okpokunou alongside Phase-1 Gas Supply

## Gas Processing Plant (GPP) – 500 MMscfd

- Extraction of Natural Gas Liquids (NGLs)

- Delivery of lean gas to downstream facilities, Includes:

  - Common front-end processing

  - Dedicated polishing units for Methanol and LNG

## Methanol Production Plant

- Two trains, each rated at 5,000 MTPD

- Total production capacity: 10,000 MTPD

## Floating LNG (FLNG) Facility/Fertilizer (Urea)

- Capacity: ~2 MMTPA LNG

- Capacity: ~2.8MMTPA UREA

- Feed gas: >200 MMscfd processed gas

- Location: ~20 km offshore, ~20 m water depth, complete with +25 km Feed Gas Supply Line from Gas Hub at AKAB to the FLNG/Fertilizer

- Products:

  - LNG/Urea

  - Condensate

  - LPG (Butane & Propane)

## Product Export System

- Export pipelines

- Offshore Single Buoy Mooring (SBM) system for methanol and NGL export

- Dry port

## Produced Water Management

- Handling, treatment, and disposal facilities

- To be defined through Decision Concept Selection (DCS) studies

## Utilities and Offsite Infrastructure

- Power generation systems

- Steam generation

- Product storage facilities

- Export jetty and marine infrastructure

- All required off-plot and support systems

## Pipeline Design Philosophy – Flexibility & Expandability

While the primary objective of the OKNU–BBOU pipeline is evacuation of Okpokunou gas production, the design incorporates provisions for future network expansion through strategically located midline manifolds, which will also function as sectionalizing valve stations.

Planned Tie-in Points:

- KP 38, - for tie-in of SEIB production:

  - Confirmed tie-in point

  - Identified as a key gas supply node

- KP 66, - for tie-in of NUNR / DBUG production:

  - Conditional tie-in, subject to future development

Given proximity and routing efficiency, SEIB is considered the most practical near-term tie-in to the OKNU–BBOU pipeline, hence the midline manifold at KP 38

For NUNR and DBUC, a shared midline manifold near DBUC, subject to firm gas supply commitments, will be more cost effective than dedicated manifolds.  The option of an independent pipeline network to gather NUNR & DBUC production to BBOU or ELEP will be evaluated during the FEED.

The Facilities Coordinates

| Location | Latitude | Longitude | KP (km) |
| --- | --- | --- | --- |
| OKNU Manifold | 5.175 | 5.846 | 0 |
| River Niger Crossing at KP 10 |  |  | 10 |
| Midline Manifold at KP 38, near SEIB |  |  | 38 |
| Midline Manifold at KP 66, near DBUC |  |  | 66 |
| BBOU Manifold | 4.478 | 6.107 | 85 |
| ELEP | 4.435 | 6.16 | 93 |
| AKAB | 4.32 | 6.405 | 125 |
| FLNG/Fertilizer | 25 km due south of AKAB (same longitude) |  |  |

# Battery Limit, and Scope of Work

## Battery Limit

The phase 1 facilities are the focus of the present FEED, however with consideration for provisions and retrofits that will accommodate the phase 2 facilities in a rather seamless manner.

The Phase-1 main facilities are:

OKNU – BBOU pipeline, 85 km

BBOU – ELEP pipeline, 8 km

ELEP - AKAB Pipeline, 32 km

OKNU Starting Manifold

BBOU Satellite Manifold

ELEP Evacuation Manifold, and

The Pipeline End Manifold at AKAB, complete with Pig Receiver.

The battery limits are shown below:

Figure 3.1 Battery Limit – Pipeline

### OKNU Platform

The terminal flanged ball valve on the manifold collecting well fluids from OKNU Wells.

The flanged ball valve provided for the tie-in of OKNU Pipeline on the manifold transporting well fluids to BBOU.

### BBOU Platform

The terminal flanged ball valve on the manifold collecting well fluids from BBOU Wells.

The flanged ball valve provided for the tie-in of Opugbene (OPUG) Pipeline on the manifold transporting well fluids to ELEP.

### ELEP Platform

The terminal flanged ball valve on the manifold collecting well fluids from ELEPA Wells.

The flanged ball valve provided for the tie-in of NUN River Pipeline on the manifold transporting well fluids to AKAB.

### Akabel Facility

The Pipeline terminal flange at the inlet to the slug catcher at AKAB.

The drain outlet flange on the pig receiver at AKAB.

## Data Room Index Structure

### Project Overview

Pipeline description

Key coordinates and KP definitions

Asset register

### Route & Survey

Alignment sheets

ROW drawings

Survey as-builts

### Pipeline Engineering

GA drawings

Isometrics

Wall thickness & specs

### Facilities

OKNU

KP38 Midline manifold

KP66 Midline manifold

BBOU

ELEP

AKAB

### Crossings

River Niger crossing

Creek crossings

HDD drawings

### Mechanical & Materials

Weld maps

Material certificates

Coating specs

### Process & Instrumentation

P&IDs

Cause & Effect

SCADA

### Electrical & CP

CP layouts

SLDs

Earthing

### Civil & Structural

Foundations

Supports

Access infrastructure

### Testing & Commissioning

Hydrotest

Drying

Pre-commissioning

### Environmental

EIA

Baseline data

Restoration plans

### Modifications

Redlines

Tie-ins

Design changes

### Decommissioning (To Be Developed)

Decommissioning Execution Plan

Cleaning & pigging procedures

Waste management plan

Restoration plan

## Layout & Configuration

### Route & Alignment

Pipeline Alignment Sheets (Plan & Profile, KP 0–125 km)

ROW Drawings (full corridor coverage)

Survey As-Built (final coordinates and deviations)

Pipeline General Arrangement (GA)

Plot Plans:

  - OKNU Manifold (KP 0)

  - BBOU Manifold (KP 85)

  - ELEP (KP 93)

  - AKAB Gas Hub (KP 125)

Pipeline Isometrics (segment-wise)

### Crossings & Special Sections

River Niger Crossing (~KP 10) drawings

Creek/River crossings (all locations)

HDD / trenchless installation drawings

Trench and burial profiles

### Mechanical & Materials

Weld maps (full traceability)

Wall thickness and coating specs

Line pipe data sheets

Material certificates (API 5L traceability)

### Valves & Facilities

Valve location drawings (chainage-based)

Pig launcher/receiver drawings

Manifold piping layouts (OKNU, KP38, KP66, BBOU, ELEP)

Slug catcher drawings

### Process & Control

As-built P&IDs (entire system)

Cause & Effect diagrams

SCADA / instrumentation layouts

### Electrical & CP

Cathodic Protection layout

Transformer Rectifier (TR) locations

Earthing & bonding drawings

Electrical Single Line Diagrams

### Civil & Structural

Foundations (manifolds, slug catchers)

Pipe supports and sleepers

Access roads and pads

### Testing & Commissioning

Hydrotest layouts and sectioning

Dewatering/drying layouts

### Environmental

Baseline environmental maps

Sensitive area mapping (mangroves, wetlands)

Restoration drawings (if applicable)

### Modifications & Deviations

Redline drawings

Tie-in modifications (KP38, KP66, BBOU integration)

Looping / resizing updates

## Submission Requirements

Digital format (PDF + native CAD)

Indexed and searchable

Linked to asset register

Verified as “As-Built” (not IFC/IFD)

## KP-by-KP Drawing Relevance (OKNU → AKAB)

This maps critical drawings to physical pipeline segments—very useful for execution planning.

### KP 0 – KP 10 (OKNU → River Niger Crossing)

- Key Features: Inlet manifold, slug catcher, swamp terrain

Required Drawings:

OKNU Plot Plan & P&IDs

Slug catcher GA

Alignment sheets

Valve and pigging drawings

CP layout

### KP 10 – River Niger Crossing

Key Features: Major river crossing (~200 m width)

Required Drawings:

HDD / crossing profile drawings

Bathymetric and geotechnical drawings

Crossing method as-built

Environmental sensitivity maps

Execution Note: High likelihood of abandonment-in-place

### KP 10 – KP 38 (Swamp Section)

Key Features: Challenging swamp terrain

Required Drawings:

Alignment + trench details

CP and coating drawings

Weld maps

Access road drawings

### KP 38 – Midline Manifold (SEIB Tie-in)

Key Features: Future tie-in node

Required Drawings:

Manifold GA and piping layout

Metering system drawings

Isolation valve drawings

### KP 38 – KP 66

Key Features: Long swamp stretch

Required Drawings:

Alignment sheets

Weld maps

CP layout

Environmental maps

### KP 66 – Midline Manifold (NUNR/DBUC Tie-in)

Key Features: Conditional tie-in

Required Drawings:

Manifold GA

Tie-in spool drawings

Instrumentation layouts

### KP 66 – KP 85 (BBOU)

Key Features: Approach to major hub

Required Drawings:

Alignment and profile

Valve segmentation drawings

Hydrotest section drawings

### KP 85 – BBOU Manifold

Key Features: Major integration node

Required Drawings:

Plot plan & P&IDs

Tie-in drawings (OKNU + ELEP line)

Metering and control systems

### KP 85 – KP 93 (BBOU → ELEP)

Key Features: Existing/planned 20” pipeline

Required Drawings:

Alignment sheets

Isometrics

CP and coating drawings

### KP 93 – KP 125 (ELEP → AKAB)

Key Features: 28” trunkline

Required Drawings:

Trunkline alignment

Weld maps

Hydrotest layouts

SCADA layouts

### KP 125 – AKAB Gas Hub

Key Features: Processing hub

Required Drawings:

Full plot plan

P&IDs

Slug catcher / inlet facilities

Export tie-ins (methanol / LNG)

# The Decommissioning & Abandonment Scope

## Governance

The exercise / process is governed be by commitment and host community satisfaction through stakeholder engagement

### Primary Regulators

- NUPRC (Nigerian Upstream Petroleum Regulatory Commission): Oversees pipelines connected to production fields and offshore platforms.

- NMDPRA (Nigerian Midstream and Downstream Petroleum Regulatory Authority): Oversees trunk lines, distribution networks, and processing plant connections.

### Core Legal Frameworks

Both regulators have issued specific 2023/2024 regulations derived from the PIA:

- Upstream: Nigerian Upstream Petroleum Decommissioning and Abandonment Regulations, 2023 (and 2024 amendments).

- Midstream/Downstream: Midstream and Downstream Decommissioning and Abandonment Regulations, 2023.

The Decommissioning & Abandonment Fund (The "Escrow")

Under the PIA, every licensee must set up a D&A Fund.

- Mandatory Contribution: You must contribute annually to an escrow account held in a commercial bank.

- Purpose: This ensures that even if a company goes bankrupt, the Nigerian government has the funds to safely remove the infrastructure.

- 2024 Update: Recent amendments allow for a portion of these funds (up to 15% for IOCs) to be held in local banks, while the rest can be in rated international institutions.

### Technical & Operational Requirements

The NUPRC and NMDPRA follow a "Comparative Assessment" model similar to the UK, but with a heavy focus on the Environmental Guidelines and Standards for the Petroleum Industry in Nigeria (EGASPIN).

Standard Procedure for Pipelines:

- Notice of Intent: You must notify the regulator at least 3 months (for specific line segments) to 36 months (for entire fields/systems) before the planned start.

- Comparative Assessment: You must provide a study comparing:

  - Total Removal: Digging up and removing the pipe.

  - Abandonment in Place: Cleaning, capping, and leaving the pipe buried.

- Cleaning & Purging: Pipelines must be flushed of all hydrocarbons using water or inert materials until they meet EGASPIN's "zero-sheen" or ppm standards.

- Sealing: Pipes must be capped at both ends with moisture-resistant materials.

- Post-Abandonment Monitoring: For pipelines left in place, the operator often remains liable for the Right of Way (RoW) and must ensure no "subsidence" (ground sinking) occurs over time.

### Key Challenges in the Nigerian Context

- Host Community Involvement: The PIA requires operators to consult with Host Community Development Trusts. You must prove that abandoning a pipeline in place won't interfere with local farming, fishing, or land use.

- Security & Vandalism: Abandoned pipelines that aren't properly "grouted" (filled with concrete) are often targeted by illegal refiners who believe residual oil remains, leading to significant environmental spills long after the line is "closed."

- Divestment Issues: If a major international oil company (IOC) sells a pipeline to a local firm, the NUPRC now strictly audits the D&A Fund to ensure the new owner can afford the eventual cleanup.

### Ancillary Systems

- Cathodic protection systems

- Electrical and SCADA systems

- Civil foundations and supports

- River and creek crossing structures

## Decommissioning Philosophy

- Safety-first execution (zero harm, zero release)

- Environmental protection (no inland discharge)

- Regulatory compliance

- Value optimization (TAR)

- Minimum disturbance in swamp terrain

## Key Decommissioning Processes

### Planning & Approvals

- Asset verification

- Environmental baseline

- Decommissioning Execution Plan (DEP)

- Regulatory and stakeholder engagement

### Shutdown & Isolation

- Controlled shutdown

- Mechanical and electrical isolation

- Segmentation into manageable sections

### Cleaning & Hydrocarbon Removal

- Depressurization

- Pigging and residue removal

- Sludge and condensate handling

### Flushing, Drying & Inerting

- Flushing (water/chemical)

- Drying (air/nitrogen)

- Nitrogen inerting

### Metering Close-Out (Critical Step)

- Final measurement reconciliation

- Calibration validation

- Data archiving and audit closure

### Disconnection & Segmentation

- Pipeline cutting and isolation

- Disconnection at all manifolds and facilities

### Execution (Removal / Abandonment)

- Segment-specific execution based on terrain and risk

### Waste Management

- Segregation and certified disposal

### Site Restoration

- Backfilling and grading

- Mangrove restoration

- Environmental monitoring

## Abandonment Activities

- Cleaning to hydrocarbon-free condition

- Permanent isolation (caps/blinds)

- Filling (water / grout / seawater)

- CP system decommissioning

- Long-term integrity assurance

- GIS updates and documentation

## KP-Based Execution Strategy

| S/N | Segment | Strategy | Justification |
| --- | --- | --- | --- |
| 1 | KP0 (OKNU) | Remove | High-value facilities (TAR) |
| 2 | KP0–10 | Mixed | Accessible sections removable |
| 3 | KP10 (River Niger) | Abandon | High environmental risk |
| 4 | KP10–38 | Abandon (majority) | Deep swamp |
| 5 | KP38 Manifold | Remove | Strategic node |
| 6 | KP38–66 | Mixed | Access-dependent |
| 7 | KP66 Manifold | Remove | Future tie-in |
| 8 | KP66–85 | Mixed | Near infrastructure |
| 9 | BBOU / ELEP | Remove | Operational hubs |
| 10 | ELEP–AKAB | Case-by-case | Depends on reuse |
| 11 | Offshore line | Abandon | Industry standard |

## Risk Management

| Risk | Mitigation |
| --- | --- |
| Residual hydrocarbons | Multi-stage cleaning + inerting |
| Environmental impact | Abandonment strategy |
| Swamp instability | Specialized equipment |
| Regulatory delays | Early engagement |
| Commercial disputes | Metering close-out |

## Conclusion

This proposal delivers a technically robust, environmentally responsible, and commercially optimized framework for decommissioning the OKNU–BBOU–ELEP–AKAB pipeline system.

It ensures:

- Safe and complete hydrocarbon removal

- Minimal environmental impact

- Full regulatory compliance

- Optimized cost through hybrid execution

- Preservation of asset value

# Key Decommissioning Processes & Abandonment Activities

## Decommissioning Processes (End-to-End Execution)

### Pre-Decommissioning Planning

- Asset verification (as-built vs actual condition)

- Regulatory approvals (Nigerian Upstream Petroleum Regulatory Commission, Nigerian Midstream and Downstream Petroleum Regulatory Authority)

- Environmental baseline and risk assessment

- Stakeholder/community engagement

### System Shutdown & Isolation

- Controlled shutdown of gas flow

- Mechanical isolation (valves, blinds, spading)

- Electrical and instrumentation de-energization

- Segmentation into manageable sections (by KP / hydrotest sections)

### Pipeline Cleaning & Hydrocarbon Removal

- Depressurization and venting

- Pigging operations:

  - Cleaning pigs

  - Batching pigs

- Chemical cleaning (if required)

- Removal of condensate, sludge, and residues

### Flushing, Drying & Inerting

- Water flushing or gel cleaning

- Air or nitrogen drying

- Nitrogen purging to achieve inert condition

### Disconnection & Mechanical Works

- Cutting of pipeline into sections

- Disconnection from:

  - Manifolds (OKNU, BBOU, ELEP)

  - AKAB gas hub

- Removal of above-ground facilities:

  - Slug catchers

  - Pigging stations

  - Metering systems

### Pipeline Removal (Where Applicable)

- Excavation (swamp-compatible methods)

- Lifting and transport

- Removal of:

  - Shallow buried pipelines

  - Congested corridor sections

- Special handling at crossings

### Waste Management

- Segregation:

  - Scrap steel

  - Hazardous waste

  - Contaminated soils

- Transport to certified disposal facilities

- Compliance with Federal Ministry of Environment standards

### Site Restoration

- Backfilling and grading

- Mangrove and vegetation restoration

- Erosion control (especially in swamp areas)

- Post-restoration monitoring

## Abandonment Activities (Pipeline Left In Place)

Applied where removal is technically difficult, environmentally risky, or uneconomic.

### Cleaning to Acceptable Standard

- Internal cleaning to remove hydrocarbons

- Verification via pigging and sampling

### Isolation & Disconnection

- Physical disconnection from live systems

- Installation of:

  - Blind flanges

  - Permanent caps

- Removal of surface tie-ins

### Filling / Stabilization

- Depending on location:

- Onshore / Swamp

- Filling with inert material:

  - Nitrogen (short-term)

  - Water or inhibited fluid

  - Cement grout (long-term stability)

- River / Offshore

- Flooding with seawater

- Natural sediment stabilization

- Rock dumping (if required)

### Cathodic Protection Decommissioning

- Deactivation of CP systems

- Removal or safe abandonment of anodes

- Electrical isolation

### Long-Term Integrity Assurance

- Corrosion risk assessment

- Monitoring (if required by regulator)

- Documentation of abandoned sections

### Marking & Records

- Updating pipeline records as “abandoned”

- GIS and survey updates

- Installation of surface markers (where required)

## Special Considerations for OKNU–BBOU–ELEP–AKAB

- High-Priority Abandonment Zones

- River Niger crossing (~KP10) → Abandon in place preferred

- Deep swamp sections (KP10–KP66) → Selective abandonment

- Offshore FLNG line → Flood & stabilize

- High-Priority Removal Zones

- Manifold areas (OKNU, KP38, KP66, BBOU, ELEP, AKAB)

- Congested corridors

- Areas with future development conflicts

# Facilities Engineering Design Features

## Pipeline Routing Philosophy

The original concept for the Okpokunou Pipeline envisaged a direct connection to the Elepa Manifold (ELEP). However, subsequent routing assessments indicated that the proposed alignment would intersect the BBOU manifold corridor and run in close parallel with the existing/planned BBOU–ELEP pipeline in the downstream section.

It is therefore considered technically and economically prudent to terminate the pipeline at the BBOU manifold and utilize the planned BBOU–ELEP pipeline segment rather than constructing a dedicated line to ELEP.

This approach offers the following advantages:

- Approximate reduction of ~ 8 km in pipeline length

- Measurable CAPEX savings

- Reduced environmental footprint

- Minimized corridor congestion

- Improved constructability within Niger Delta swamp terrain

## Liquid Management Strategy

### Upstream Liquid Removal

The base case concept provides for removal of the majority of entrained liquids upstream at Okpokunou in order to:

- Reduce hydraulic loading

- Improve flow stability

- Minimize slugging risk

- Optimize downstream pipeline sizing

Accordingly, a slug catcher is proposed at Okpokunou.

### Diameter Optimization

Early liquid removal may permit optimization of pipeline diameter. However, final sizing will be confirmed during FEED through:

- Steady-state hydraulic modeling

- Transient multiphase simulation

- Comparative evaluation of alternate slug catcher locations (inlet vs midline vs outlet)

- Sensitivity cases for turndown and ramp-up scenarios

## Receiving Facility Protection

A slug catcher at the Pipeline End Manifold (PLEM) will provide protection against liquid slugs,   thereby safeguarding downstream processing equipment and ensuring stable plant operations.

## Liquid Handling and Disposal

The slug catcher facility will include full liquid-handling systems comprising:

- Condensate/NGL transfer facilities to AKAB for processing

- Produced water collection and handling system

- Storage and metering as required

- Produced water disposal options will include:

- Offshore discharge (subject to regulatory compliance)

- De-mineralisation for industrial use

- Other approved beneficial reuse options

Discharge into inland waters is not permissible under NUPRC and FMEnv regulations.

## Pipeline Capacity and System Integration

The pipeline will be designed to transport up to 300 MMscfd of raw wellhead natural gas, made up as follows:

1. Design Throughput

The pipeline will be designed for a maximum capacity of 300 MMscfd of raw wellhead natural gas, comprising:

- 200 MMscfd from the RAEC-DSV Gas Sales and Purchase Agreement

- 70 MMscfd make-up gas on RAEC 270 MMscfd, in case the 70 MMscfd production will be coming from the fields whose production will be tied-in to the Okpokunou pipeline, or even from Okpokunou itself.

- 30 MMscfd design allowance, - for production upside

- Total Design Capacity: 300 MMscfd

The 300 MMscfd will flow to the BBOU manifold, from where the gas will join the BBOU enroute to ELEP via an existing/planned 20” x 8km to the ELEP M/F, enroute through 28-inch × 32 km trunkline to the Akabel Gas Processing Hub. At Akabel, the gas will be processed as feedstock for a Methanol Manufacturing Plant.

## System Integration

Gas will flow:

- From OKNU to BBOU via the proposed 20” x ~ 85 km pipeline

- From BBOU through an existing/planned 20” × ~8 km line to ELEP

- From ELEP through a 28” × ~ 32 km trunkline to the Akabel Gas Processing Hub

At Akabel, the gas will be processed as feedstock for a Methanol Manufacturing Plant.

The OKNU–BBOU pipeline shall therefore be designed to reliably transport up to 300 MMscfd under all operating scenarios, while maintaining full flow assurance across the integrated OKNU–BBOU–ELEP–AKAB pipeline network, ensuring delivery of the target 500 MMscfd to the Gas Hub.

## Pipeline Routing and Terrain

The approximately 85 km pipeline will traverse challenging Niger Delta swamp terrain and include:

- One major crossing of the River Niger, (a distributary of the Niger River), estimated at:

  - 200 m width

  - 9 m water depth

- Four (4) additional river crossings

- Eight (8) creek crossings

- Standard inlet manifold facilities at OKNU

- Terminal manifold facilities at BBOU

Special crossing methodologies (e.g., HDD, microtunneling, or cofferdam/trench methods) will be evaluated during FEED based on geotechnical and bathymetric investigations.

## Pipeline Size Decision

The pipeline diameter shall be selected as the optimum commercial size capable of reliably transporting the forecast gas volumes to BBOU at a delivery pressure sufficient to ensure that the combined streams from BBOU arrive at the Gas Plant inlet at the required 60 barg.

The final diameter will be established through integrated hydraulic and flow assurance modelling of the full export corridor, including:

- OKNU–BBOU pipeline (new design subject line, currently assessed at 20” – 24”)

- Existing Design 20” BBOU–ELEP pipeline, currently assessed at 20” – 24”

- Existing Design 28” ELEP–AKAB pipeline, currently assessed at 30” – 32”

System-wide validation will confirm that the selected diameter sustains the target throughput while maintaining pressure, temperature, and operability margins across all operating scenarios. Should modelling indicate hydraulic or flow assurance constraints within the downstream segments, re-sizing of the affected sections will be evaluated to preserve system integrity and performance.

Where the hydraulically optimal diameter differs materially from the commercially efficient size, competing options shall be comparatively assessed based on:

- Capacity robustness and future expansion potential

- Flow assurance risks (liquids handling, turndown, slugging, hydrate margin)

- CAPEX and lifecycle OPEX implications

- Constructability and swamp terrain constraints

- Uncertainty in production forecast and ramp-up profile

The selected diameter will therefore represent a balanced, risk-informed decision that optimizes commercial viability, operational reliability, and long-term system flexibility.

## Metering System

### Wet Gas Metering (For Hydrocarbon Accounting)

Hydrocarbon accounting will primarily be based on the contractual RAEC wet gas meters, to which BFPCL is granted full (“unfettered”) access under the GSPA, including integration into its Control System.

To ensure measurement assurance and data validation, BFPCL will deploy a limited number of independent check meters. These are discretionary and intended solely for reconciliation purposes, not custody transfer.

The optimized check metering philosophy is as follows:

- Elepa (Pipeline Inlet): One check meter installed at pipeline entry (Pipeline FEED scope).

- Akabel (Pipeline Outlet): One check meter at pipeline discharge to the slug catcher (Pipeline FEED scope).

- GPP Inlet (Slug Catcher): Check meters at both gas and liquid legs feeding the GPP train (GPP FEED scope).

### The Fiscal Metering system

The wet gas meters at delivery points form part of the overall fiscal framework. However, fiscal metering in this context specifically refers to processed (lean) gas and associated fluids.

- Fiscal metering facilities (gas, condensate, and produced water) are designated for RAEC but will be located within the GPP and jointly operated by BFPCL and RAEC, in accordance with the GSPA.

- Meter duplication is to be avoided; therefore, any additional BFPCL-installed meters will be strictly for reconciliation and performance monitoring (e.g., simple mass flow meters).

- Laboratory data from BFPCL will be integrated into the reconciliation process to enhance accuracy and auditability.

### Other Metering Systems

BFPCL will independently design and install metering systems for gas streams allocated to methanol production and utilities.

- The preferred metering technology is ultrasonic flow metering, capable of accurately determining both flow rate and energy content at plant entry.

- Final selection and inclusion within the GPP vendor scope will be confirmed during detailed engineering.

### Governance & Integration

- A Joint Operations Team (Upstream–Midstream interface) will be established, covering the full chain from wellhead to GPP, in line with the GSPA.

- All metering systems included in the GPP bid will be reviewed and rationalized to ensure clarity of purpose and eliminate redundancy.