GAS PROCESSING & METHANOL COMPLEX PROJECT NO. BFPCL-DSV-RAEC 2026

| Project | FEED for Gas Gathering Pipelines, Gas Processing Plant & Methanol Plant |
| --- | --- |
| Client | Brass Fertilizer and Petrochemical Company Limited |
| Originating Company | Epic Atlantic Limited |
| Document Title | Produced Water Handling, Processing, & Disposal Philosophy |
| Document Number | EA-BFPCL-DSV-GGPL-FEED-GEN-PHY-004 |
| Document Revision | R03 |
| Document Status | Issued as a Requirement |
| Originator | Obima Joe Oragwu |
| Endorsement | Aloy Onyenucheya Duru, COREN (R.7580) |
| Security Classification | Restricted |
| Issue Date | 09-May-26 |

Produced Water Handling, Processing, & Disposal Philosophy

| R03 | 08 May 2026 | Review Update | Joe Oragwu | Joe Oragwu / Aloy Duru | Aloy Duru COREN (R.7580) | Cyril Akika |
| --- | --- | --- | --- | --- | --- | --- |
| R02 | 25 Mar 2026 | Review Update | Joe Oragwu | Joe Oragwu / Aloy Duru | Aloy Duru COREN (R.7580) | Cyril Akika |
| R01 | 07 Mar 2026 | Issued for Review | Joe Oragwu | Joe Oragwu / Aloy Duru | Aloy Duru COREN (R.7580) | Cyril Akika |
| Rev # | Issue Date | Status Description | Originator | Reviewer | Endorsement (Epic) | Approval (BFPCL) |

Revision History

| Rev No. | Date | Description of Revision |
| --- | --- | --- |
| R01 | 07 Mar 2026 | For Review by RAEC, and Subsequent Discussion with NUPRC, in respect of BBOU & ELEP FDP |
| R02 | 25 Mar 2026 | Clarification that clearly brings out BFPCL options plan without ambiguity |
| R03 | 09 May 2026 | Updated to include Zero Liquid Discharge and River Water Intake |
| A01 |  |  |

Revision Philosophy:

- All documents for review shall be issued at R01, with subsequent R02, R03, etc as required.

- All documents approved for issue or approved for design shall be issued at A01 with subsequent A02, A03, etc. as required. (Management of Change is required for A02, A03, etc.)

for the subsequent project phases, post FEED, it is expected that:

- All Detailed Design documents for review shall be issued at D01, with subsequent D02, D03, etc. as required.

- All documents approved for construction shall be issued at C01 with subsequent C02, C03, etc. as required. (Management of Change is required for C02, C03, etc.)

- All approved “As-Built” documents shall be issued at Z01, with subsequent Z02, Z03, etc as required. (Use versions Z01.1, Z01.2, Z01.3, etc to review the “As-Built” document to Z02).

Restricted

This document is made available subject to the condition that the recipient will neither use nor disclose the contents except as agreed in writing with the copyright owner.  Copyright is vested in Brass Fertilizer and Petrochemical Company Limited (BFPCL) © All rights reserved.

Neither the whole nor any part of this document may be reproduced or distributed in any form or by any means (electronic, mechanical, reprographic, recording, or otherwise) without the prior written consent of the copyright owner.

SUMMARY PAGE

| Client: | Brass Fertilizer and Petrochemical Company Limited |  |
| --- | --- | --- |
| Project: | FEED for Gas Gathering Pipelines, Gas Processing Plant & Methanol Plant | Project No. BFPCL-DSV-RAEC 2026 |
| Facility: | Gas Gathering Pipelines, Gas Processing Plant & Methanol Plant | Doc No. EA-BFPCL-DSV-GGPL-FEED-GEN-PHY-004 |

This document demonstrates BFPCL/DSV Management plan and commitment to follow the regulatory & policy framework towards produced water handling, treatment and disposal.  To this effect BFPCL/DSV has developed a Plan, including Framework, Road Map and Decision Flow Charts, Benchmarks and Best practices, for systems, procedures, and controls for safe handling, treatment, monitoring, and disposal of produced water generated in the project.

The Produced Water will come from 3 streams on the 125km pipeline, namely: OKNU-BBOU, BBOU-ELEP and ELEP-AKAB production streams.

Produced water will be generated from three principal sources: the upstream wells, the gas processing facilities, and the methanol production plant, with an initial combined volume estimated at approximately 30 MBWPD. This is below the methanol plant’s total water demand requirement of 40 MBWPD for sustained operations.

Accordingly, a key operational challenge will be the identification and integration of supplementary water sources to bridge the estimated shortfall of approximately 10 MBWPD. The additional water, together with the available produced water stream, will require appropriate treatment and conditioning to achieve the necessary industrial water quality specifications for continuous and reliable plant operation.

Potential supplementary water sources may include surface water, groundwater, municipal supply, seawater desalination, or third-party industrial water supply, subject to technical feasibility, regulatory approvals, environmental considerations, and overall project economics. The combined water streams will subsequently be processed through the plant’s water treatment facilities for reuse as industrial utility and process water within the methanol complex.

BFPCL/DSV is committed to full regulatory compliance in alignment with the reference documents below:

The Water Treatment will start with 3-phase Separator, followed by a cascade of downstream treatment units designed to progressively remove oil, suspended solids, and fine particulates.

Six options will be evaluated as part of the concept selection & detail design, viz:

- Industrial Re-use (The Core Goal): Produced water is treated to ultra-high purity levels as steam feedstock for the 10,000 MTPD Methanol Plant., Achieves Zero Liquid Discharge

- Hybrid: Re-use + BR Transfer (18km): Produced water from AKAB Terminal piped 18km pipeline to the nearby Brass Terminal to dispose surplus water at reduced capex

- Hybrid: OKNU Source Sep + Barge: Water & condensate separated upstream the 125km trunkline and moved by barges to the AKAB Terminal.

- Hybrid: OKNU Source Sep + Spiking:. Separated condensate/water re-injected into the gas for for multiphase flow in the 125km pipeline to AKAB Terminal

- Offshore Outfall & Emergency Hybrids: Dedicated 22.2km subsea pipeline leads from the AKAB Terminal to a deep-water diffuser to dispose the waters

- .3rd Party Outsourcing: The liability for water disposal is shifted to a contractor, who collects, treats & disposes the water at their own government-approved facilities but at high opex.

.

| REferences |  |
| --- | --- |
| Document No. | Description |  |
| EA-BFPCL-GMMC-GGPL-FEED-GEN-RPT-002 | Basis of Design |  |
|  | Petroleum Industry Act (2021) |  |
|  | EGASPIN (administered by NUPRC) |  |
|  | EIA Act |  |
|  | National Oil Spill Detection and Response Agency (NOSDRA Act) |  |
|  | National Environmental Standards and Regulations Enforcement Agency (NESREA Act) |  |

Table of Contents

Abbreviations	7

1.	Executive Summary	10

2.	Introduction	11

2.1	Background Information	11

2.2	Schematics of FEED Scope	13

3.	Regulatory Standards and Requirements	14

3.1	Regulatory Instruments	14

3.2	Regulatory Standards / Limits	14

3.2.1.	Disposal Methods in NUPRC Guidelines	14

3.2.2.	Effluent Discharge Limits (2026)	16

3.3	Regulatory Monitoring and Reporting Requirements	16

3.3.1.	Statutory Operational Control	16

3.3.2.	Monitoring & Reporting Obligations	16

3.3.3.	Technical & Operational Verification	17

3.3.4.	Regulatory Compliance Roadmap	17

3.3.5.	Produced Water Characterization	17

3.3.6.	Treatment & Processing Technologies	17

3.3.7.	Handling and Processing Standards	18

3.3.8.	Technical Handling for Gas & Methanol Wastewater	18

4.	BFPCL Framework & Implementation	20

4.1	BFPCL Framework	20

4.2	BFPCL Roadmap	20

4.2.1.	Process Integrated Sequence	23

4.2.2.	Plant Water Management Decision Flow Chart	23

5.	Produced Water Characterisation & Risk Assessment	25

5.1	Background Information	25

5.1.1.	Source & Composition	25

5.1.2.	Environmental & Health Risk Assessment	25

5.1.3.	Data & Monitoring Plan	25

5.2	Treatment & Management Strategies	25

5.2.1	Source Reduction & Production Practices	25

5.2.2	On-Site Treatment Technologies	25

5.2.3	Off-Site / Advanced Options	26

5.3	Water Reuse & Resource Optimization	26

5.3.1.	Internal Reuse	26

5.3.2.	Beneficial Reuse Opportunities	26

5.4	Monitoring, Reporting & Compliance Assurance	26

5.4.1	Environmental Monitoring	26

5.4.2	Reporting	26

5.4.3	Corrective Actions	26

5.5	Stakeholder Engagement & Community Safeguards	26

5.5.1	Community Consultation and HCDT Framework	27

5.5.2	Grievance Mechanisms	27

5.5.3	Capacity Building	27

5.6	Research, Innovation & Continuous Improvement	27

5.6.1	Technology Trials	27

5.6.2	Standards Review	27

5.6.3	Collaborative Initiatives	27

5.7	Summary of Best Practices	27

6.	Produced Water Management Policy	29

6.1	Scope	29

6.2	Discharge Standards	29

6.3	Produced Water Management Hierarchy	29

6.3.1	Prevention & Minimization	29

6.3.2	Reuse & Reinjection	29

6.3.3	Treatment & Controlled Discharge	29

6.3.4	Disposal	29

6.4	Technical Standards	29

6.4.1	Characterization	29

6.4.2	Treatment Philosophy	30

6.5	Monitoring & Reporting	30

6.5.1	Monitoring Requirements	30

6.5.2	Reporting	30

6.5.3	Risk Management & Incident Response	30

6.6	Community & Environmental Safeguards	31

6.7	Governance & Accountability	31

6.8	Continuous Improvement	31

7.	PRODUCED WATER VOLUME MANAGEMENT	32

7.1	Produced Water Volumes	32

7.1.1	Peak Water Consumption Analysis	32

7.2	River Water Intake	32

Regulatory Implications of the "Water Gap"	32

Since you now require supplemental water, your regulatory burden expands beyond disposal:	32

7.3	Strategic FDP Justification	32

7.4	Treatment Philosophy & Process Design	33

7.4.1	Treatment Objectives	33

7.4.2	Process Description	33

7.4.3	Chemical Treatment	33

7.4.4	Monitoring Systems	34

7.5	Disposal Strategy	34

7.5.1	Industrial Re-use	34

7.5.2	Contingency Discharge	34

7.6	Compliance With Discharge Limits	34

7.7	Environmental Risk Assessment	34

7.8	Monitoring & Reporting	35

7.8.1	Sampling Frequency	35

7.8.2	Reporting	35

7.9	Sludge & Waste Management	35

7.10	Integrity Management	35

7.11	Emergency Response	35

7.12	Training & Governance	35

7.13	Decommissioning & Abandonment	37

8.	CONCLUSION	38

## Abbreviations

| Abbreviation | Meaning |
| --- | --- |
| AKAB | Akabel |
| AOP | Advanced Oxidation Process |
| API | American Petroleum Institute |
| ASU | Air Separation Unit |
| ATR | Autothermal Reformer |
| BBOU | Bubouwe Bou Field |
| BFPCL | Brass Fertilizer and Petrochemical Company Limited |
| BOD | Biochemical Oxygen Demand |
| BTEX | Benzene, Toluene, Ethylbenzene, and Xylene |
| BWPD | Barrels of Water Per Day |
| CAP | Corrective Action Plan |
| Cd | Cadmium |
| COD | Chemical Oxygen Demand |
| COREN | Council for the Regulation of Engineering in Nigeria |
| CF | Cartridge Filter |
| CPF | Central Processing Facility |
| Cr | Chromium |
| DAF | Dissolved Air Flotation |
| DGF | Dispersed Gas Flotation |
| DMF | Dual Media Filter |
| DSV | DSV Pipetronix Limited |
| DW-01 | Disposal Well 01 |
| ECMR | Environmental Compliance Monitoring Report |
| EA | Epic Atlantic (Document Prefix) |
| EGASPIN | Environmental Guidelines and Standards for the Petroleum Industry in Nigeria |
| EIA | Environmental Impact Assessment |
| ELEP | Elepa Field |
| EOR | Enhanced Oil Recovery |
| EPF | Early Production Facility |
| ESG | Environmental, Social, and Governance |
| FDP | Field Development Plan |
| Fe | Iron |
| FEED | Front-End Engineering Design |
| GGPL | Gas Gathering Pipelines |
| GOSP | Gas-Oil Separation Plant |
| GPMC | Gas Processing & Methanol Complex |
| GPP | Gas Processing Plant |
| GSPA | Gas Supply and Purchase Agreement |
| HAZOP | Hazard and Operability Study |
| HSE | Health, Safety, and Environment |
| IGF | Induced Gas Flotation |
| ISO | International Organization for Standardization |
| IX | Ion Exchange |
| LOF | Life-of-Field |
| MBWPD | Thousand Barrels of Water Per Day |
| MEG/TEG | Monoethylene Glycol / Triethylene Glycol |
| MMscfd | Million Standard Cubic Feet per Day |
| MSDS | Material Safety Data Sheet |
| MTPD | Metric Tonnes Per Day |
| NESREA | National Environmental Standards and Regulations Enforcement Agency |
| NGL | Natural Gas Liquids |
| Ni | Nickel |
| NIWA | National Inland Waterways Authority |
| NOSDRA | National Oil Spill Detection and Response Agency |
| NUPRC | Nigerian Upstream Petroleum Regulatory Commission |
| OEMS | Online Effluent Monitoring System |
| OIW | Oil-in-Water |
| OKNU | Okpokunou Field |
| OML | Oil Mining Lease |
| Pb | Lead |
| PAH | Polycyclic Aromatic Hydrocarbons |
| PIA | Petroleum Industry Act |
| PWMP | Produced Water Management Plan |
| RAEC | Regulatory Affairs and Environmental Compliance |
| RCA | Root Cause Analysis |
| RENAISSANCE (RAEC) | Renaissance Africa Energy Company Limited |
| RO | Reverse Osmosis |
| RWIS | River Water Intake Skid |
| SDI | Silt Density Index |
| SBM | Single Buoy Mooring |
| SCADA | Supervisory Control and Data Acquisition |
| S/C | Steam-to-Carbon Ratio |
| SMR | Steam Methane Reformer |
| TDS | Total Dissolved Solids |
| TSS | Total Suspended Solids |
| TVD | True Vertical Depth |
| WTP | Water Treatment Plant |
| WTU | Water Treatment Unit |
| ZLD | Zero Liquid Discharge |

# Executive Summary

This document outlines BFPCL’s management philosophy and commitment to comply with the applicable regulatory and policy framework governing produced water handling, treatment, and disposal.

Produced water will be generated from three principal sources: the upstream wells, the gas processing facilities, and the methanol production plant, with an initial combined volume estimated at approximately 30 MBWPD. This is below the methanol plant’s total water demand requirement of 40 MBWPD for sustained operations.

Accordingly, a key operational challenge will be the identification and integration of supplementary water sources to bridge the estimated shortfall of approximately 10 MBWPD. The additional water, together with the available produced water stream, will require appropriate treatment and conditioning to achieve the necessary industrial water quality specifications for continuous and reliable plant operation.

Potential supplementary water sources may include surface water, groundwater, municipal supply, seawater desalination, or third-party industrial water supply, subject to technical feasibility, regulatory approvals, environmental considerations, and overall project economics. The combined water streams will subsequently be processed through the plant’s water treatment facilities for reuse as industrial utility and process water within the methanol complex.

Produced Water comes from 3 sources: 1) formation water from wet gas gathering wells run through a 125km pipeline network, 2) condensed water recovered during the gas dehydration and cooling processes within the 500 MMscfd Gas Processing Plan  (GPP) and 3)  "Reaction Water" generated as a byproduct of the methanol synthesis process of the 10,000 MTPD Methanol Plant (MP).  Both plants are at the AKAB Terminal

Six water handling, treatment and disposal options are considered. The preferred option is the Industrial Re-use of the produced water by the Methanol Plant. Produced water from all sources are treated by a central Water Treatment Plant (WTP) at AKAB equipped with Double Pass Reverse Osmosis (RO) and Ion Exchange modules to process the water to ”Boiler Feedwater Quality.” A methanol Stripper removes methanol from the reaction water before it gets to the MP Steam Methane Reformers. (SMR). At peak operations level, all the produced water may be consumed by the MP and for Utility/Firewater/Toilets, transitioning the project to Zero Liquid Discharge (ZLD).

In the event of surplus water, more than can be consumed by the MP, the surplus water will be disposed through the offshore outfall Option, Regional transfers or by marine shuttle exports to third parties, Such event may occur as a result of downtime for plant maintenance, during operations ramp-up stages, when only one train of 5000 MTDP MP is operational before the construction of the second train, etc,

A High-Capacity Finger Slug Catcher at AKAB hub to handle even surges in slugs.

BFPCL’s objective is to ensure full regulatory compliance and environmental stewardship, in alignment with the following Nigerian statutory and regulatory instruments:

- Petroleum Industry Act

- Environmental Guidelines and Standards for the Petroleum Industry in Nigeria administered by the Nigerian Upstream Petroleum Regulatory Commission

- Environmental Impact Assessment Act

- National Oil Spill Detection and Response Agency Act

- National Environmental Standards and Regulations Enforcement Agency Act

The Produced Water management will be based on regulatory compliance, environmental protection, operational reliability, lifecycle cost, and long-term field development strategy.

# Introduction

  - Background Information

Brass Fertilizer and Petrochemical Company Limited (BFPCL) is developing a 10,000 metric tonnes per day (MTPD) capacity greenfield methanol production facility in Akabel (AKAB) in Odioma, Brass LGA, Bayelsa state. The plant complex is to focus on phase-1 production of natural gas feedstock from 2 RAEC fields, - Elepa (ELEP) & Bubouwe Bou (BBOU) in OML 33, anchored on GSPA 270, and the import is the production from these two fields.

In as much as the focus is on BBOU & ELEP, we would like to draw our attention to Okpokunou (OKNU) production, anchored on a separate GSPA 200 which would invariably impact on produced water volumes, hence the water handling, processing, and disposal plan.

It is therefore of pragmatic imperative that Okpokunou production be included in the produced water handling, processing, and disposal plan in BBOU & ELEP, as the OKNU productions would be happening at the same time as BBOU & ELEP.

The Project involves the development, construction, and operation of a plant comprising:

Two trains of 5,000 MTPD methanol plant, producing a total of 10,000 MTPD of methanol

500 MMscfd Gas Processing Plant (“GPP”), which will extract NGL from the natural gas feedstock, prior to feeding the lean gas to the methanol plant.

Gas gathering pipelines and associated manifolds – BBOU-ELEP-AKAB Pipelines, comprising a combination of 20” x 8km BBOU-ELEP Pipeline Segment + 28” x 32km ELEP-AKAB Pipeline, and the 20” x 85km OKNU-BBOU pipeline

Product Export Lines and SBM for the export of the methanol, and NGL of the GPP.

All offsite, utility, and off-plot facilities (including product storage, internal power generation, steam generation, and export jetty) for the operation of the processing plants.

Produced water is generated from 3 sources, with initial production of 36 Mbwpd, increasing up to 40 Mbwpd over life of field (LOF).

Wells Crude Production: Elepa, and Bubouwe Bou, and Okpokunou crude production; and under a separate GSPA 200, from formation water.  Initial water production will be 36 Mbwpd and will increase, as the field matures, up to, 40 Mbwpd over life-of-field (LOF).

Gas Processing Plant: Water knock out from 500 MMscfd from a temperature drop from 40°C to 15°C from propane refrigeration or JT valves & condensate water mix.

Methanol Plant: “Reaction Water” -byproduct of CO2 hydrogenation in methanol production or syngas production

The produced water will be:

Treated to meet EGASPIN discharge limits administered by NUPRC.

Primarily re-injected into a designated disposal well, if available..

Surface discharged only under contingency conditions and within regulatory limits.

The treatment system will be designed with +30% capacity margin and redundancy to ensure continuous compliance. Online oil-in-water (OIW) monitoring and automatic diversion systems will be included.

BFPCL commits to full regulatory compliance, environmental protection, and continuous monitoring in accordance with applicable Nigerian regulations.

  - Schematics of FEED Scope

Schematics: - Phase-1 Gas Supply from BBOU & ELEP alongside Okpokunou Gas Supply

Satellite Imagery: - Phase-1 Gas Supply from BBOU & ELEP alongside Okpokunou Gas Supply

# Regulatory Standards and Requirements

  - Regulatory Instruments

Key governing instruments include:

- Petroleum Industry Act (PIA) 2021

- Environmental Guidelines and Standards for the Petroleum Industry in Nigeria (EGASPIN)

- NUPRC Upstream Petroleum Environmental Regulations

- Applicable DPR legacy guidelines (where referenced)

- National Environmental (Surface & Groundwater Quality Control) Regulations

  - Regulatory Standards / Limits

    - Disposal Methods in NUPRC Guidelines

The disposal methods recommended under the current NUPRC regulations are outlined below. All identified methods have been duly considered in the BFPCL produced water treatment, handling, and disposal study, and have informed the development of the primary disposal pathways evaluated:

| Method | Regulatory Status | Requirements |
| --- | --- | --- |
| Re-injection | Preferred | Water is pumped back into the reservoir for pressure maintenance. Requires NUPRC approval and integrity tests. - Into depleted reservoirs or designated disposal wells - Requires reservoir compatibility study - Must prevent formation damage and groundwater contamination - Continuous pressure monitoring required |
| Industrial Re-use | Preferred | - Approval of WTP Engineering Design & EIA - Inspection of Online Monitoring Systems (OEMS) - Monthly Effluent Quality Reports (EQR) - Environmental Evaluation Report (EER) |
| Surface Discharge (Onshore/Swamp Conditions) | Restricted | Discharging into freshwater rivers is increasingly discouraged. - Only after full treatment - Must meet EGASPIN effluent standards - Discharge point must be environmentally approved - Diffuser systems required in some cases |
| Offshore Discharge | Permitted | Allowed beyond a certain distance from the shoreline, provided oil content is within the 40 mg/L limit. - Online Oil-in-Water (OIW) analyzers installed that provide a continuous data feed to NUPRC and - an Automatic Diverter Valve triggered by the 40mg/L limit, sending the contaminated water back to a "slop tank" rather than into the ocean. |
| Evaporation / Containment | Limited Use | - Requires lined pits - No unlined earthen pits permitted - Must prevent seepage to groundwater |

    - Effluent Discharge Limits (2026)

Regulations differentiate strictly between Inland/Nearshore (high-risk swamp and land areas) and Offshore (deep sea) operations; the following limits will be observed:

| Parameter | Inland / Nearshore | Offshore* |
| --- | --- | --- |
| Oil & Grease | < 10 mg/L | < 30 mg/L |
| Total Dissolved Solids (TDS) | < 2,000 mg/L | Ambient Seawater levels |
| Chemical Oxygen Demand (COD) | < 125 mg/L | Monitoring required |
| BOD (Biol. Oxygen Demand) | < 30 mg/L | < 50 mg/L |
| Phenols | < 0.5 mg/L | < 1.0 mg/L |
| Methanol Content | < 2.0 mg/L (Residual) | < 5.0 mg/L |
| pH | 6.5 – 8.5 | 6.5 – 8.5 |
| Heavy Metals (Pb, Hg, Cr) | Near-zero / Non-detectable | Strictly monitored |
| Turbidity | < 10 NTU | N/A |
| Temperature | Ambient ± 3°C | Ambient ± 5°C |

*>12 nautical miles / 22.2km

  - Regulatory Monitoring and Reporting Requirements

    - Statutory Operational Control

As a responsible corporate entity, BFPCL will implement the following requirements:

- Environmental Management Plan (EMP): will be prepared and approved to demonstrate how produced water will be minimized and treated.

- Environmental Risk Register (ERR): of potential water-related risks (e.g., pipe bursts, treatment failure) will be maintained.

- NUPRC Quarterly Effluent Monitoring & Reports (ECMR):

- Produced water management plan (PWMP)

- The Environmental Remediation Fund (ERF) from Section 103 of the PIA, all operators must contribute to enable the NUPRC to clean up the site immediately.

- Real-time monitoring (where applicable)

- Flow meters on discharge lines

- Secondary containment for treatment systems

- Sludge handling and hazardous waste disposal procedures

- Emergency spill response plan

- Host Community Development Trust, all operators must contribute 3% annual opex  to this fund

    - Monitoring & Reporting Obligations

BFPCL in compliance with statutory requirements will implement the following:

- Monthly effluent reporting to NUPRC

- Annual Environmental Performance Report

- Environmental audit every 3 years

- Immediate reporting of non-compliance events

- Record retention for regulatory inspection

Failure to comply may attract:

- Administrative penalties

- Suspension of operations

- Environmental remediation orders

    - Technical & Operational Verification

To stay compliant, BFPCL like other operators in the Niger Delta must now implement:

- Continuous Monitoring: Real-time sensors for Oil-in-Water (OIW) content.

- Quarterly Bioassays: Testing the toxicity of treated water on local aquatic species (e.g., tilapia or shrimp) every 3 months.

- Integrity Audits: Annual pressure testing of re-injection wells to ensure produced water isn't leaking into freshwater aquifers.

    - Regulatory Compliance Roadmap

To ensure your project remains "audit-ready" BFPCL will implement:

- Baseline Study: Ensure the Environmental Impact Assessment (EIA) that specifically covers the chemical footprint of methanol byproducts, not just oil.

- Water Balance Audit: the NUPRC-required  "Water Map"—showing how many barrels of water enter the plant vs. how many are recycled or disposed of.

- Facility Commissioning: BFPCL invite NUPRC/NMDPRA for a "Pre-Commissioning Inspection" of the treatment plant before starting production.

    - Produced Water Characterization

BFPCL will:

- Conduct full physicochemical analysis

- Determine oil-in-water (OIW) concentration

- Measure heavy metals, TDS, BTEX, PAHs, salinity, and naturally occurring radioactive materials (NORM)

- Establish baseline environmental data before discharge

Routine sampling and laboratory certification are mandatory.

    - Treatment & Processing Technologies

- Primary physical separation 
 Gravity separation, API oil–water separators, hydrocyclones, and dissolved gas/air flotation (DGF/DAF) systems remove bulk oil and suspended solids before advanced treatment.

- Secondary & tertiary treatment
. Adsorption using activated carbon or local bio-adsorbents (e.g., modified agricultural wastes like banana or orange peels) can reduce hydrocarbons and metals. 
• Membrane filtration (micro-, ultra-, nano-filtration) targets dissolved contaminants and polishing to meet discharge criteria. 
• Biological methods (e.g., constructed wetlands, algal photobioreactors, SBRs with microalgae) offer eco-friendly polishing and nutrient removal.

- Modular hybrid systems
• Combining gravity, biological, and membrane units can achieve higher pollutant removal in a compact footprint suitable for onshore Niger Delta sites.

- Reuse and beneficial application
• Treated produced water can be reused for oilfield operations (e.g., drilling fluids, fracture water) or industrial non-potable uses, reducing freshwater demand and disposal volumes.

    - Handling and Processing Standards

Produced water in the Niger Delta is highly saline and contains hydrocarbons, heavy metals, and production chemicals. The Regulatory mandate of a multi-stage treatment process will be followed:

Treatment Objectives

Technologies like hydrocyclones, gas flotation units, and filtration will be used to meet specific effluent limits before any form of release. Key limits include:

- Oil & Grease Content: Typically limited to 30 mg/L for nearshore/inland and 40 mg/L for offshore (though recent NUPRC directives push for stricter <10-20 mg/L in sensitive swamp areas).

- Salinity (TDS): Must be monitored; inland discharge is generally restricted if it significantly alters the salinity of freshwater ecosystems.

- Heavy Metals: Strict limits on Lead, Mercury, and Chromium to protect the Niger Delta's biodiversity

    - Technical Handling for Gas & Methanol Wastewater

Because the water isn't just "oily" but contains dissolved chemicals, standard hydrocyclones aren't enough. Our facility will deploy:

- Stripping Columns: To recover dissolved methanol from process water before it enters MP Steam Reformer Feed or the waste stream. This is both a "Wealth" (product recovery) and "Compliance" (COD reduction) move.

- Biological Aerated Filters (BAF): Bacteria are used to "eat" the residual methanol and glycols (TEG/MEG) in the water.

- Advanced Oxidation Processes (AOP): Using ozone or UV/H₂O₂ to break down complex chemicals that bacteria can't digest.

# BFPCL Framework & Implementation

  - BFPCL Framework

The Company’s Framework encompasses:

- Road Map and Decision Flow Charts,

- Benchmark & Best Practices towards compliance;

- Benchmark & Best Practices towards continuous improvement that will strengthen regulatory standing and ESG positioning:

- Target ≤ 20 mg/L OIW (international best practice)

- Adopt hydrocyclones + induced gas flotation systems

- Implement reinjection where feasible (reduces surface discharge risk)

- Deploy digital monitoring & SCADA integration

- Conduct regular third-party lab verification

- Align with ISO 14001 Environmental Management Systems

- Standard Operating Procedures (SOPs), including Key Performance Indicators (KPIs):

- Development of Procedures & Methods

- Controls for Safe Handling, and Treatment,

- Monitoring, and Disposal of produced water generated in accordance to Petroleum Industry Act (2021)

- Key Performance Indicators (KPIs)

- Oil-in-Water: < 10-20 mg/l

- TSS: < 5-30 mg/l

- Reinjection-Ready Design

- Strategic Value, including:

- ESG Risk Reduction

- Regulatory Compliance Alignment

- Scalable for High Water-Cut

- Recommended Treatment Flow:

- Separation  Hydrocyclone  Induced Gas Flotation  Dual Media Filter  Cartridge Filter  2-Stage Reverse Osmosis  Ion Exchange  Reuse

  - BFPCL Roadmap

The Road map considers 6 concept selections (see table below) to be evaluated as part of detail design:

Industrial Re-use of the produced water has been adjudged the best option.  It utilizes all the well-produced water from wet gas pushed all along the 125km, the produced water from both the 500 MMscfd Gas Processing Plant (GPP) and the 10,000 MTPD Methanol Plant (MP). This complies with the NURPC Zero Liquid Discharge (ZLD) strategy for 2026.  At full operation, the water requirement for the methanol plant industrial loop will be barely met, which means zero water balance for discharge.

The features of this option include; a high-capacity finger type slug catcher at AKAB hub to manage possible slug surges and a central Water Treatment Plant (WTP) with the process flow given below.

| Priority | Option | Key Facilities | Sub-Facilities | CAPEX (Est.) | Pros | Cons | Regulator Ease (NUPRC/NMDPRA) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Industrial Re-use (The Core Goal) | Central WTP & MP Utility Loop | St Nicholas RWIS, AOP, Methanol Stripper, 2-Stage RO, IX | $68M - $85M | Sustains 10k MTPD steam needs; Guaranteed reliability via River Intake. High ESG rating | Highest technical complexity; requires "Electronic-Grade" purity; else “Catalyst Poisoning” | Highest: Aligns with PIA 2021 Circular Economy & Green Industry mandates. |
| 2 | Hybrid: Re-use + BR Transfer | Inter-Terminal Pipeline (8") | AKAB Pumping Skid, LACT Metering, TPA Contract | $12M - $18M | Lowest cost synergy for Phase 1 surplus water. | Dependent on Third Party Access (TPA) and neighbor uptime. | High: Regulators favor "Facility Sharing" to minimize environmental footprint. |
| 3 | Hybrid: OKNU Source Sep + Barge | OK Hub Loading Jetty & Storage | Hydrocyclones at OKNU Hub, Double-hull Barges | $30M - $45M | Protects 125km trunkline from salt/corrosion at the source. | Security risks in the St Nicholas/Brass creeks; high OPEX. | High: Proactive waste management before trunkline transport. |
| 4 | Hybrid: OK Source Sep + Spiking | Multiphase Trunkline (125km) | AKAB Finger Slug Catcher (15k bbl), HP Injection Pumps | $35M - $40M | Minimal upstream footprint; utilizes existing gas corridor. | High corrosion risk; massive liquid handling at AKAB Terminal. | Moderate: Requires high-spec leak detection & telemetry monitoring. |
| 5 | Offshore Outfall & Emergency | 22.2km Marine Pipeline | Offshore Pumps, Neutralization Tank, Diffuser Heads | $22M - $28M | Ultimate disposal resilience; handles RO Brine & IX waste. | Perception of discharge; requires strict NMDPRA/ECMR monitoring. | Moderate: Approved strictly as a secondary or maintenance backup. |
| 6 | 3rd Party Outsourcing | On-site Reception & Loading | Transfer Pumps, Custody Meters, Contractor Vessels | $12M - $18M | Shifts technical/compliance burden to a contractor. | Highest per-barrel "Gate Fees"; zero control over disposal. | Low: Regulators prefer operators to own their entire waste lifecycle. |

This option is combined with the Offshore Outfall option   or the Transfer to Brass Terminal or barging to third party to dispose of redundant water. Excess water may occur during plant downtimes for maintenance, delayed start-up of second train or high water-cuts from wells in later years of life.

The well re-injection (PWRI) option has not been considered since there are no wells available for it.

    - Process Integrated Sequence

| Step | Unit Operation | Primary Function | Technical Output / Goal | Operational Risk (Failure Consequence) |
| --- | --- | --- | --- | --- |
| 1 | Slug Catcher & 3-Phase Sep | Primary gravity separation of Gas, Oil, and Water. | Stabilized Feed: Removal of 99% bulk liquids. | Slug Overload: Liquid carry-over into GPP, causing immediate plant trip. |
| 2 | De-oiling (Hydrocyclone / IGF) | Centrifugal & buoyancy-driven oil removal. | OIW < 20 ppm: Protection of downstream filter media. | Media Fouling: Oil coats filters and RO membranes, requiring total replacement. |
| 3 | Filtration (DMF/Cartridge) | Depth filtration and 1–5 micron safety barrier. | SDI < 3: Elimination of physical particulates / silt. | Membrane Abrasion: Silt/sand punctures RO membranes, leading to salt passage. |
| 4 | Methanol Stripper | Thermal recovery of Methanol and VOCs. | Product Recovery: Prevention of RO bio-fouling. | Bio-fouling: Organic "food" creates bacterial slime, plugging the RO system. |
| 5 | Advanced Oxidation (AOP) | UV + H2​O2​ destruction of trace organics. | TOC < 0.2 ppm: Elimination of BTEX/PAHs. | Catalyst Coking: Trace organics "crack" into soot, destroying Reformer catalysts. |
| 6 | Reverse Osmosis (2-Pass) | Molecular desalination via semi-permeable membranes. | 99% TDS Removal: Primary mineral reduction. | Scaling: Mineral buildup (Calcium/Silica) on membranes, reducing water flow. |
| 7 | Ion Exchange (Mixed Bed) | Final polishing of residual ions/minerals. | "Electronic-Grade": Cl < 0.05 ppm; Silica < 0.01 ppm. | Catalyst Poisoning: Trace Chlorides cause irreversible chemical deactivation of ATR/SMR. |
| 8 | SMR + ATR Reforming Block | Catalytic conversion of dry gas + ultra-pure steam. | Stoichiometric Syngas: Target H2​/CO ratio. | Production Loss: Low-quality steam causes emergency shutdown of 10,000 MTPD plant. |
| 9 | Neutralization & Outfall | pH balancing of RO Brine and IX waste. | Regulatory Compliance: Meeting NMDPRA standards. | Regulatory Fine: Discharge of aggressive waste leads to environmental penalties/fines. |

    - Plant Water Management Decision Flow Chart

# Produced Water Characterisation & Risk Assessment

  - Background Information

    - Source & Composition

Produced water typically contains:

- High salinity and dissolved solids

- Hydrocarbons (oil & grease), organic compounds

- Heavy metals (Fe, Pb, Ni, Cr, etc.)

- Other inorganic constituents

These contaminants vary by field and over time and often exceed regulatory limits without treatment.

    - Environmental & Health Risk Assessment

- Toxicity to ecosystems: Untreated produced water can harm aquatic life and soil quality, affecting fisheries and agriculture.

- Human exposure risks: Communities relying on surface/groundwater can be adversely affected if produced water is improperly discharged.

    - Data & Monitoring Plan

- Baseline sampling: Establish pre-production water quality baselines.

- Routine testing: Frequent sampling of produced water for parameters like oil & grease, TDS, metals, BOD/COD.

- Trend analysis: Use time-series data to detect deterioration or spikes in contaminants.

  - Treatment & Management Strategies

A robust produced water management strategy combines prevention, treatment, reuse, and disposal.

    - Source Reduction & Production Practices

- Downhole oil-water separation: Separates water before reaching surface facilities, reducing downstream handling volumes.

- Reservoir management: Reduce water cut through well interventions and pressure maintenance to minimize produced water volumes.

    - On-Site Treatment Technologies

A layered approach combining physical, chemical, and biological treatment:

- Primary separation: Gravity separators or Gas-Oil Separation Plants (GOSP) remove bulk oil and water phases.

- API separators: Used for initial removal of free oil and suspended solids.

- Induced gas flotation & skimming: Enhance removal of dispersed oil droplets.

- Chemical dosing: Demulsifiers, coagulants and flocculants assist aggregation of pollutants.

- Adsorption & filtration: Media filters (e.g., walnut shell filters), bio-adsorbents (groundnut shells, sugarcane bagasse, etc.) can reduce metals and residual hydrocarbons.

- Biological treatment: Emerging techniques using microbes or algae can reduce organic loads.

    - Off-Site / Advanced Options

- Reinjection for disposal or EOR: Treated water can be reinjected into subsurface formations for disposal or reservoir pressure support.

- Zero Liquid Discharge (ZLD) approaches: Advanced evaporation/desiccation technologies can eliminate liquid discharge and generate solid by-products.

  - Water Reuse & Resource Optimization

    - Internal Reuse

- Operational reuse: Use treated produced water for drilling, work-overs, or pressure maintenance where permitted.

- Reduced freshwater demand: Prioritize reuse to mitigate freshwater consumption, especially in water-scarce zones.

    - Beneficial Reuse Opportunities

- Agricultural irrigation or industrial uses: Only if water quality meets safe reuse thresholds and community consent.

- Community supply potential: Explore long-term treatment pathways that could support local water demands, subject to stringent safety standards.

  - Monitoring, Reporting & Compliance Assurance

    - Environmental Monitoring

- Continuous monitoring systems at discharge points.

- Performance checks for treatment systems.

- Independent audits and third-party verification where appropriate.

    - Reporting

- Periodic compliance reports to NUPRC & environmental regulators.

- Public transparency on water quality and management performance.

    - Corrective Actions

- Non-compliance triggers mandatory review and mitigation plans.

- Incident response plans in case of spills or accidental discharges.

  - Stakeholder Engagement & Community Safeguards

    - Community Consultation and HCDT Framework

- Regular engagement with host communities on environmental concerns, water impacts, and management plans.

- The project must establish a Host Community Development Trust (HCDT) via the HostComply portal.

- Funding: 3% of the actual annual Operating Expenditure (OPEX).

    - Grievance Mechanisms

- Establish clear channels for communities to report water quality issues or grievances.

- Grievance Redress: A formal tracker must be maintained; environmental grievances must be acknowledged within 48 hours.

    - Capacity Building

- Support local training and education on produced water risks and safeguards

- .Skills Acquisition: Training curriculum must be OGTAN-certified and registered on the NCDMB NOGIC JQS portal. Key modules include Pipeline Surveillance and Methanol Safety.

  - Research, Innovation & Continuous Improvement

    - Technology Trials

Pilot novel treatment and reuse technologies, including bio-adsorbents and advanced separation systems.

    - Standards Review

Regularly update local discharge and reuse criteria to align with international best practices and emerging science.

    - Collaborative Initiatives

Industry-government partnerships for data sharing, research and sustainable water management strategies.

  - Summary of Best Practices

- Strict compliance with environmental regulations and effluent limits.

- Comprehensive characterization of produced water to inform treatment design.

- Implementation of layered treatment systems combining physical, chemical, and biological methods.

- Promotion of reuse and resource optimization to reduce freshwater demand.

- Robust monitoring, reporting, and adaptive management to ensure long-term compliance.

- Meaningful stakeholder engagement, especially with local communities.

# Produced Water Management Policy

  - Scope

This policy applies to:

  - All onshore, swamp, and shallow offshore assets in the Niger Delta

  - Flow stations, central processing facilities (CPF), early production facilities (EPF)

  - Produced water handling, storage, treatment, reuse, discharge, and reinjection systems

  - Contractors and third-party operators

  - Discharge Standards

Produced water shall not be discharged unless it meets prescribed limits for:

  - Oil & Grease

  - Total Suspended Solids (TSS)

  - Total Dissolved Solids (TDS)

  - pH

  - Heavy Metals (Fe, Pb, Cr, Ni, Cd, etc.)

  - Temperature

Stricter limits apply for inland/swamp discharge compared to offshore discharge.

  - Produced Water Management Hierarchy

The Company adopts the following hierarchy (highest priority first):

    - Prevention & Minimization

  - Reservoir management to reduce water cut

  - Well interventions to control water production

    - Reuse & Reinjection

  - Pressure maintenance

  - Enhanced Oil Recovery (EOR)

  - Operational reuse (drilling/workover fluids)

    - Treatment & Controlled Discharge

  - Multi-stage treatment systems

  - Continuous monitoring before discharge

    - Disposal

  - Approved subsurface disposal wells

  - No uncontrolled surface discharge

  - Technical Standards

    - Characterization

Produced water shall be characterized for:

- Hydrocarbon content

- Salinity

- Metals

- Naturally Occurring Radioactive Materials (where applicable)

- Dissolved gases

Baseline environmental data must be established before production.

    - Treatment Philosophy

A multi-barrier treatment approach shall be implemented:

Stage 1 – Primary Separation

- Three-phase separators

- Heater treaters

- Free water knockouts

Stage 2 – Secondary Treatment

- Hydrocyclones

- Induced Gas Flotation (IGF) units

- Skim tanks

Stage 3 – Tertiary/Polishing

- Media filters (e.g., walnut shell filters)

- Cartridge filters

- Adsorption systems

- Chemical polishing

Discharge is permitted only after compliance verification.

  - Monitoring & Reporting

    - Monitoring Requirements

- Daily operational monitoring

- Weekly laboratory analysis (minimum)

- Continuous Oil-in-Water analyzer at discharge point

- Quarterly third-party validation

    - Reporting

- Monthly compliance reports to NUPRC

- Immediate reporting of exceedances

- Annual environmental performance report

    - Risk Management & Incident Response

- Produced water spill response plan aligned with NOSDRA requirements

- Secondary containment for storage tanks

- Emergency shutdown systems

- Root cause analysis for any exceedance

  - Community & Environmental Safeguards

- Stakeholder engagement prior to discharge approvals

- Public grievance mechanism

- Protection of wetlands, mangroves, fisheries, and groundwater

- No discharge into potable water sources

  - Governance & Accountability

| S/N | Role | Responsibility |
| --- | --- | --- |
|  | Asset Manager | Overall compliance |
|  | Production Superintendent | Operational integrity |
|  | Environmental Manager | Monitoring & reporting |
|  | HSE Team | Audit & training |
|  | Contractors | Compliance with this policy |

  - Continuous Improvement

- Annual performance review

- Technology upgrades evaluation

- Water reuse expansion targets

- Benchmarking against international best practice

# PRODUCED WATER VOLUME MANAGEMENT

  - Produced Water Volumes

The total produced water volume is given in the table below:

| Source | Volume (BWPD) | Type |
| --- | --- | --- |
| Wet Gas Wells | 36,000-40,000 | Formation Brine (Saline) |
| GPP Condensation | 2,500 – 4,000 | High Purity Condensate |
| MP Reaction Water | 9,500 – 12,500 | Process Byproduct (Organic-rich) |
| TOTAL INT SUPPLY | 52,000 – 56,500 | Total available for Re-use |
| Total Consumption | 82,000 | Ultra-Pure Steam |
| Water Gap | 25,500 | River Water Intake |

    - Peak Water Consumption Analysis

For a 10,000 MTPD plant using Combined Reforming (SMR + ATR), the peak water demand is driven by the Steam-to-Carbon (S/C) ratio.

- Peak Demand: ~1.3 tons of high-purity water per ton of Methanol.

- Daily Metric Volume: 13,000 Metric Tons/Day.

- Volumetric Equivalent: ~82,000 Barrels Per Day (BPD).

| Parameter | Current | Peak Forecast |
| --- | --- | --- |
| Average Daily | 36,000 bwpd | 40,000 BWPD |
| Design Capacity | 52,000 BWPD | — |

System designed with +30% contingency capacity.

  - River Water Intake

- Regulatory Implications of the "Water Gap"

- Since you now require supplemental water, your regulatory burden expands beyond disposal:

- River Water Intake Permit: Required from the NIWA (National Inland Waterways Authority) and the NMDPRA.

- Water Footprint Reporting: The volume of water extracted from the St Nicholas River vs. the volume of Produced Water re-used must now be reported in the ECMR.

- Brine Management: Even with 82,000 BPD consumption, the RO Brine (~20,000 BWPD) and IX Waste (~800 BPD) must still be discharged via the Offshore Outfall.

  - Strategic FDP Justification

The water management strategy for the 500 MMscfd Bayelsa Hub is engineered for Total Resource Optimization, utilizing a high-efficiency Two-Step Reforming (SMR + ATR) configuration that requires a peak ultra-pure steam load of 82,000 BWPD The project leverages the gas gathering network as a primary 'water mine,' providing ~56,500 BWPD of internal supply (well brine, condensation, and reaction water) supplemented by a dedicated St Nicholas River Intake Skid to guarantee feedstock reliability regardless of well-water fluctuations. This internal supply is secured by a 'Triple-Shield' treatment strategy—integrating Methanol Stripping, Advanced Oxidation (AOP), and Ion Exchange—to destroy trace organics (BTEX) and achieve 'electronic-grade' purity. This technical 'insurance' ensures maximum protection for multi-million dollar synthesis catalysts and extends the operational lifespan of the facility to 20+ years, while the 22.2km Offshore Outfall provides the ultimate disposal resilience to maintain uninterrupted gas production under all operational scenarios.

  - Treatment Philosophy & Process Design

    - Treatment Objectives

- Reduce OIW to ≤ 20 mg/L

- Remove suspended solids

- Control scaling and corrosion

- Enable safe reinjection

    - Process Description

Produced Water Treatment Integrated Sequence:

- Three-Phase Separator: Primary gravity separation of gas, liquid hydrocarbons, and formation brine from the OKNU-BBOU-ELEPA-AKAB gathering lines.

- Hydrocyclone Package: Centrifugal de-oiling to reduce bulk oil-in-water (OIW) concentrations.

- Induced Gas Flotation (IGF): Polishing stage using gas-bubble buoyancy to remove residual emulsified oil.

- Dual Media Filters (DMF): Depth filtration to remove suspended solids, protecting the downstream stripping and oxidation units.

- Methanol Stripper: Thermal recovery unit that extracts dissolved methanol from the MP Reaction Water and GPP Condensate for recycle, while removing volatile organics from the well water.

- Advanced Oxidation Process (AOP): Integration of UV and H2O2 to destroy recalcitrant organics (BTEX/PAHs) that survive stripping, protecting the RO membranes from bio-fouling.

- Cartridge Polishing Filters: Fine safety barrier to ensure a Silt Density Index (SDI) < 3.0.

- Double Pass Reverse Osmosis (RO): Bulk desalination stage removing 99%+ of bulk Chlorides  and Total Dissolved Solids (TDS).

- Ion Exchange (IX): Mixed-bed polishing to achieve "electronic-grade" purity (Chlorides <0.05 ppm).

- SMR + ATR Reforming Block: The destination for the treated 82,000 bwpd stream. The water is converted to high-pressure steam and reacted with the 500 MMscfd gas feed to produce Syngas.

    - Chemical Treatment

- Demulsifier

- Corrosion inhibitor

- Scale inhibitor

- Biocide (controlled dosage)

All chemicals approved and MSDS attached.

    - Monitoring Systems

- Online Oil-in-Water analyzer

- Flow meters

- Pressure indicators

- High-OIW alarm & automatic diversion to slop tank

  - Disposal Strategy

    - Industrial Re-use

Produced water will be recycles for industrial use by the Methanol Plant.

Process sequence will follow section 7.2.2 above

    - Contingency Discharge

If reinjection unavailable:

- Treated water discharged to controlled outfall

- Discharge point coordinates documented

- OIW continuously monitored

- Immediate shutdown if limits exceeded

  - Compliance With Discharge Limits

System designed to meet:

- Oil in Water: ≤ 29 mg/L

- No visible sheen

- TSS within EGASPIN limits

- Heavy metals within allowable thresholds

Design target OIW: ≤ 15 mg/L (internal standard)

  - Environmental Risk Assessment

HAZOP conducted on produced water system.

Identified risks:

- Separator upset

- IGF failure

- Pipeline rupture

- Sludge overflow

Mitigation measures:

- Redundant pumps

- Secondary containment

- Automated shutdown

- Spill kits at discharge point

Environmental sensitivity assessment confirms proximity to mangrove ecosystem; therefore, reinjection prioritized.

  - Monitoring & Reporting

    - Sampling Frequency

- OIW: Continuous monitoring

- Full lab analysis: Monthly

- Heavy metals: Quarterly

    - Reporting

- Monthly compliance report to NUPRC

- Annual Environmental Performance Report

- Immediate notification to NUPRC and NOSDRA in case of exceedance

  - Sludge & Waste Management

Estimated sludge generation: 1.2 m³/day.

Management:

- Stored in closed sludge tank

- Removed quarterly

- Disposed via licensed waste contractor

- Waste manifest documentation maintained

  - Integrity Management

- Corrosion coupons installed

- Chemical dosing optimization

- Quarterly pipeline inspection

- Cathodic protection system installed

  - Emergency Response

Integrated with Oil Spill Contingency Plan.

In event of exceedance:

- Immediate diversion

- Shut down discharge

- Notify NUPRC within regulatory timeframe

- Root cause investigation

  - Training & Governance

- Environmental Officer appointed

- Operators trained quarterly

- Competency matrix maintained

- Internal audit conducted annually

  - Decommissioning & Abandonment

At end-of-field, Decommissioning & Abandonment will follow the table below;

| S/N | Asset | Removal Strategy |
| --- | --- | --- |
|  | Offshore Outfall (22km) | Flushing & Retrieval. |
|  | 125km OKNU-AKAB Trunkline | Cleaning & In-situ Capping. |
|  | Water Treatment Plant (WTP) | Dismantling & Remediation. |
|  | River Water Intake Skid | Dismantling & Remediation |
|  | Gas Processing Plant (GPP) | Dismantling & Remediation. |
|  | Methanol Plant (MP) | Dismantling & Remediation. |
|  | Brass Export Terminal | Dismantling & Remediation. |

Final environmental closure report submitted

# CONCLUSION

BFPCL confirms that produced water generated at OML 33 will be:

- Properly characterized

- Adequately treated

- Preferentially recycled in Industrial Re-use to achieve Zero Liquid Discharge (ZLD)

- Continuously monitored

- Fully compliant with NUPRC regulatory requirements

The system will be designed with environmental protection as the primary objective in this sensitive Niger Delta swamp environment.

Top of Form

Bottom of Form