## Chklist n Specs - Gas Pipelines
Scope Of Work Checklist & Specifications - Gas Gathering Pipelines
Date | 2025-12-15
|  | SYSTEM / SUBSYSTEM |  |  |  | WORK SCOPE SPECIFICATION | NOTES
A | Engineering & Design
| 1 | Pipeline Route & RoW Engineering
|  | 1.1 | Route surveys, soil assessments, geotechnical evaluation |  |  | Full topographical survey using GPS/Total Station; swamp geotechnical investigation including boreholes, cone penetration tests (CPT), soil classification, moisture content, shear strength; hydrology & flood-level mapping; identification of unstable/peat zones; soil corrosivity assessment for CP design; integration of survey data into GIS-based route model
|  | 1.2 | Development of alignment sheets and pipeline profile drawings |  |  | Preparation of alignment sheets showing horizontal/vertical route geometry, chainage, bend points, RoW width, crossings, CP test posts, FOC routing, ground elevation profile, and geotechnical layers. Drawings prepared per ISO 128/CAD standards; integration with GPS coordinate system and BOD MAOP/design factor inputs
| 2 | Line Pipe Specifications
|  | 2.1 | 28" ELEP-AKAB Pipeline |  |  | CS, API 5L X70 PSL2 Linepipes (28", WT 20.62 mm).
|  | 2.2 | 18" BBOU-ELEP Pipeline |  |  | CS, API 5L X70 PSL2 Linepipes (18", WT 11.91 mm).
| 3 | Pipeline Length & Design Calculations
|  | 3.1 | 28" ELEP-AKAB Pipeline |  |  | Length 32 km, in swamp, cutting 3 major river crossings Taking off from ELEP M/F with PIG Facilities (Pig Launcher) Terminating at Pig Receiver at P/L end Facility at AKAP
|  | 3.2 | 18" BBOU-ELEP Pipeline |  |  | Length 8 km, in swamp, cutting 1 river crossing Taking off from BBOU M/F with PIG Facilities (Pig Launcher) Terminating at Pig receiver at ELEP M/F
|  | 3.3 | Wall thickness, stress analysis, hydraulic modelling, surge analysis |  |  | Wall thickness & stress verification per ASME B31.8; material properties per API 5L (X70) and EN10204 MTCs; hydraulic steady-state modelling and transient/surge analysis using recognized software (e.g., PIPEPHASE/OLGA); corrosion allowance per BOD; design for MAOP = 110 barg; apply design factor 0.6 and safety margins per BOD/ASME B31.8.
| 3 | Crossing Design
|  | 3.1 | Roads, waterways, other pipelines, utilities, with HDD or open cut where required |  |  | Crossing design per API RP 1102 (waterways) and HDD vendor standards; HDD bore sizing ≥ 1.5× pipe OD for pullback allowance; scour protection and bedding per geotechnical recommendations; road/utility crossings to use casing or concrete encasement per local highway/utility authority; crossing construction methodology documented in crossing method statements.
|  | 3.2 | Crossing of Lagos-Calabar Coastal Road |  |  | Crossing Philosophy: HDD (base case method) and Microtunneling (fallback method, but subject to geotechnical confirmation). Strategic preference for the pipeline to be installed prior to road construction as engagement with the Federal Ministry of Works (Nigeria) would primarily focus on: i) Agreement on minimum burial depth ii) Mechanical protection requirements iii) Compliance with applicable highway crossing regulations If the road is constructed first, trenchless crossing (HDD or microtunnel) will be mandatory.
| 4 | Valve Station Design
|  | 4.1 | In-line valves and block valve stations |  |  | Valve station design per ASME B31.8: valves to be API 6D full-bore, rated ≥ MAOP (110 barg) with 1.5× test margin; implement double-block-and-bleed where required; actuator selection per IEC 60034 (motors) and IEC 60079 for hazardous area equipment; include blow-down, drains and depressurisation arrangements; layout per BOD valve spacing / accessibility requirements.
B | Procurement & Fabrication
| 1 | Line Pipe
|  | 1.1 | API 5L line pipe procurement
|  |  | 1.1.1 | 28" line pipe |  | API 5L, Steel Grade- X70MS, WT- 20.62mm, Coating- 3LPE, Design pressure= 110barg, Design Factor= 0.6, ANSI Class= 900#, NPS=28".
|  |  | 1.1.2 | 18" line pipe |  | API 5L, Steel Grade X70 MS, WT- 11.91mm, Coating 3LPE, Design pressure= 110barg, Design Factor= 0.6, ANSI Class= 900#, NPS=18".
|  | 1.2 | Linepipe joints |  |  | Full penetration butt welds; WT matching pipe; weld procedures per project WPS; weld repair <3%; Includes welded ends prepared for field welding
|  | 1.3 | Linepipe steel |  |  | API 5L, Steel Grade- X70MS; For planning—use actual mill weights for procurement
| 2 | Pipeline Components
|  | 2.1 | Bends |  |  | Long-radius bends per ASME B16.49; material ASTM A860 WPHY-70; coating 3LPE per ISO 21809
|  | 2.2 | Fittings- Elbows, Tees, Reducers, Weld O'lets, sockolets |  |  | Elbows/Tees/Reducers: ASME B16.9; Sockolets: ASME B16.11; Weldolets: MSS SP-97; Materials: ASTM A234 WPB/WPHY-70; Coating: 3LPE ISO 21809
|  | 2.3 | Flanges | 18" line pipe |  | ASME B16.5 (≤24") / ASME B16.47 (Series A/B for >24"); Class 900; Material ASTM A105/A350 LF2; Spiral-wound gaskets ASME B16.20
|  | 2.4 | Isolating joints | 28" line pipe |  | Monolithic isolation joints per ISO 18849; Material ASTM A105; Suitable for 110 barg; 3LPE coating
|  | 2.5 | Gaskets | 18" line pipe |  | Spiral-wound SS316/Graphite per ASME B16.20; Soft gaskets per ASME B16.21
|  | 2.6 | Bolts and nuts | 28" line pipe |  | ASTM A193 B7 bolts; ASTM A194 2H nuts; Hot-dip galvanized; Class 900 flanges
|  | 2.7 | Spools / Pups |  |  | Fabricated at yard and installed in-line; Pup lengths 300–600 mm; same material grade X70; used for tie-ins; BE/BE ends
| 2 | Manifolds
|  | 2.1 | ELEP Manifold
|  |  | 2.1.1 | PIG Launcher - 28"/32", complete with Closure Door |  | Design Pressure 110 barg; Minor Barrel 28", Major 32"; Closure Door per ASME VIII Div 1; Materials ASTM A516 Gr 70 / X70MS; Coating: 3LPE; Internal epoxy lining optional per EPC
|  |  |  | 2.1.1.1 | Accessories & Bulk Materials, -Fittings, Bends, Elbows, Gauges, Valves, Isolation joints, Flanges | Flanges ASME B16.47; Fittings ASME B16.9/11; Gaskets ASME B16.20; Valves API 6D; Gauges per ISO 5167/ASME MFC; Insulating joints per ISO 18849
|  |  | 2.1.2 | PIG Receiver - 28"/32", complete with Closure Door |  | Design Pressure 110 barg; Minor Barrel 28", Major 32"; Closure Door per ASME VIII Div 1; Materials ASTM A516 Gr 70 / X70MS; Coating: 3LPE; Internal epoxy lining optional per EPC , code stamped ASME VIII; PV Elite design; hydrotest at 1.5× MAWP = 165 barg
|  |  |  | 2.1.2.1 | Accessories & Bulk Materials, -Fittings, Bends, Elbows, Gauges, Valves, Isolation joints, Flanges | Flanges ASME B16.47; Fittings ASME B16.9/11; Gaskets ASME B16.20; Valves API 6D; Gauges per ISO 5167/ASME MFC; Insulating joints per ISO 18849
|  |  | 2.1.3 | Vessels and Tanks- Drain tanks, NGL vessels, Cartridge filters |  | Closed drain drum: 1m × 3m T/T, design pressure 7 barg; Open drain tank: 2m × 1m × 1m; Filters per ASME VIII; Material: Carbon steel SA-516 Gr 70; Corrosion allowance 3 mm
|  |  | 2.1.4 | Midline slug catcher |  | Horizontal slug catcher; inlet size 28"; design pressure 110 barg; slug capacity sized per flow (typically 5–10 m³); Includes tie-in spools & drainage
|  | 2.2 | AKAB End Manifold
|  |  | 2.2.1 | PIG Receiver - 28"/32", complete with Closure Door |  | Design Pressure 110 barg; Minor Barrel 28", Major 32"; Closure Door per ASME VIII Div 1; Materials ASTM A516 Gr 70 / X70MS; Coating: 3LPE; Internal epoxy lining optional per EPC
|  |  |  | 2.2.1.1 | Accessories & Bulk Materials, -Fittings, Bends, Elbows, Gauges, Valves, Isolation joints, Flanges | Flanges ASME B16.47; Fittings ASME B16.9/11; Gaskets ASME B16.20; Valves API 6D; Gauges per ISO 5167/ASME MFC; Insulating joints per ISO 18849
|  |  | 2.2.2 | Vessels and Tanks- Drain tanks, NGL vessels, Cartridge filters |  | Closed drain drum: 1m × 3m T/T, design pressure 7 barg; Open drain tank: 2m × 1m × 1m; Filters per ASME VIII; Material: Carbon steel SA-516 Gr 70; Corrosion allowance 3 mm
|  |  | 2.2.3 | Spur lines / kicker lines to PEF/slug catcher |  | Includes spool pieces and bypass lines; Size 4"–10" typical; MAOP 110 barg; material API 5L Grade X52/X60
|  | 2.3 | BBOU Manifold
|  |  | 2.3.1 | PIG Launcher - 18"/22", complete with Closure Door |  | Design pressure 110 barg; Minor 18", Major 22"; ASME VIII; 3LPE; Material X70MS or SA-516 Gr 70
|  |  |  | 2.3.1.1 | Accessories & Bulk Materials, -Fittings, Bends, Elbows, Gauges, Valves, Isolation joints, Flanges | Flanges ASME B16.5; Fittings ASME B16.9/11; Gaskets ASME B16.20; ISO 5167 instrumentation
|  |  | 2.3.2 | PIG Receiver - 18"/22", complete with Closure Door - Provisional |  | Design pressure 110 barg; Minor 18", Major 22"; ASME VIII; 3LPE; Material X70MS or SA-516 Gr 70
|  |  |  | 2.3.2.1 | Accessories & Bulk Materials, -Fittings, Bends, Elbows, Gauges, Valves, Isolation joints, Flanges | Flanges ASME B16.5; Fittings ASME B16.9/11; Gaskets ASME B16.20; ISO 5167 instrumentation
|  |  | 2.3.3 | Vessels and Tanks- Drain tanks, NGL vessels, Cartridge filters |  | Closed drain vessel size- 1m x 3m T/T Open drain tank size- 2m x 1m x 1m (L x W x H) Design pressure of 7 barg for both the closed drain vessel & vent stack and atmospheric pressure for the open drain tank
| 3 | Valves & Stations
|  | 3.1 | Actuated valves, pipeline instrumentation, Metering station |  |  | API 6D valves; ASME B16.34 class 900; Actuators: IEC 60034 motors; Positioners: IEC 61511; Valve face-to-face ASME B16.10
|  | 3.2 | Pipeline isolation valves |  |  | API 6D full-bore ball valves; Fire-safe per API 607; 3LPE coating
|  | 3.3 | Check valves and MOVs |  |  | Check valves API 6D swing type; MOV per IEC 61508 SIL compliance;
|  | 3.4 | Block valves 28", full bore |  |  | ASME Class 600+; piggable; actuator-ready; body A105/A350 LF2
| 4 | Coating & Cathodic Protection (CP) Materials
|  | 4.1 | Fusion Bonded Epoxy (FBE), 3LPE, joint coating equipment |  |  | 3LPE per ISO 21809; FBE per AWWA C213; Joint coatings with heat-shrink sleeves
|  | 4.2 | Cathodic Protection System |  |  | Temporary: Sacrificial anodes per NACE SP0169; Permanent: ICCP system per NACE RP0176; Test posts every 500 m
| 5 | Fibre Optic Cable (FOC) & Conduit
|  | 5.1 | 48-core fibre optic cable |  |  | ITU-T G.652.D single-mode fibre; armoured; UV-resistant jacket
|  | 5.2 | FOCC (fibre optic cable conduit) |  |  | HDPE conduit, Schedule 40 equivalent; buried alongside pipeline
|  | 5.3 | Marker posts |  |  | UV-stabilised polyethylene, reflective labels
| 6 | AC Mitigation System Materials
|  | 6.1 | AC-mitigation cable |  |  | 4-core 90 mm², 11 kVA, XLPE insulated cable
|  | 6.2 | Earthing rods and grounding conductors |  |  | Copper-bonded rods, 3 m; Earthing grid per IEEE 80
| 7 | Pipeline Crossings Materials
|  | 7.1 | HDD casing pipe |  |  | Steel casing API 5L Gr B; WT = ≥12.7 mm; Coating: FBE; Welded joints
|  | 7.2 | Casing spacers & seals |  |  | High-density polymer spacers; Insulating type
|  | 7.3 | River crossing supports |  |  | Structural steel per ASTM A36; corrosion-resistant paint (epoxy)
| 8 | Pigging Materials
|  | 8.1 | PIG Launcher / Receiver |  |  | All pigs: polyurethane disc/brush type, bi-directional, clearing debris
|  | 8.2 | Pipeline pigs for cleaning / gauging
|  | 8.3 | Pig launch accessories
| 9 | Construction Equipment & Consumables
|  | 9.1 | Welding rods, grinding wheels, sand for padding |  |  | Welding rods- E7018 rods; Grinding wheels EN 12413; Washed sand for padding
|  | 9.2 | Construction equipment for swamp (Marsh buggies, swamp/bog mats, amphibious excavators, pontoons) |  |  | i) Marsh buggies: Load capacity 5–12 t, low ground pressure ≤ 0.5 psi, articulated chassis, min ground contact area to avoid sinkage; coral/galvanised undercarriage ii) Swamp/bog mats: Mat panels 3.0–6.0 m long × 2.0–3.0 m wide; thickness 50–80 mm laminated timber/HDPE composite; bearing capacity ≥ 20 t/m² per mat configuration; interlocking system for continuous track iii) Amphibious excavators: Operating weight 15–30 t; pontoon width adjustable; bucket sizes 0.5–1.5 m³; swing torque per vendor iv) Pontoons;Modular pontoons 2.5–6 m long, buoyancy per module ≥ 2 t, galvanized steel or HDPE; deck load rating 2–5 t/m²; mooring points & D-rings
|  | 9.3 | Dewatering pumps, generators, NDT equipment |  |  | i) Dewatering pumps: Diesel or electric submersible/centrifugal; capacity 200–2,000 m³/hr (select per zone); head up to 40–60 m; solids handling up to 50 mm; API 610 for larger pumps ii) Generators: Diesel gensets 50–500 kVA depending on site; automatic start; bunded fuel storage; emissions control per local regs iii) NDT equipment: Portable UT/PA, RT film or digital radiography, MPI & PT kits; UT calibration blocks; RT exposure calculation charts
| 10 | Provision for Factory Acceptance Test (FAT) |  |  |  | FAT per API 6D (valves), ASME VIII (pressure vessels), IEC 61511 (instrumentation)
| 11 | Instruments
|  | 11.1 | Pressure Transmitter, Temperature Transmitter, Flow Transmitter |  |  | Transmitters ¦ 4–20 mA/HART; SIL-2 per IEC 61508/61511; Enclosure IP66
| 12 | Fabrication Scope
|  | 12.1 | Pre-fabrication of tie-in spools |  |  | Tie-in spools Fabrication per ASME B31.8; NDT 100% RT/UT; 3LPE field joints
|  | 12.2 | Fabrication of pipeline risers & valve assembly spools |  |  | Spools Fabrication per ASME B31.8; NDT 100% RT/UT; 3LPE field joints
|  | 12.3 | Fabrication of HDD casing assemblies & River crossing structural supports | 18" line pipe |  | Designed for HDD loads; per API 5L; Coating FBE
|  | 12.4 | Fabrication of CP Test Stations (CP cable terminations & mounting posts) | 28" line pipe |  | PVC test post; wiring to junction box; CP cable termination per NACE SP0572
|  | 12.5 | Fabrication of FOC Marker Systems | 18" line pipe |  | As per telecom spec ITU-T
|  | 12.6 | Fabrication of rollers, supports, saddles, frames | 28" line pipe |  | Structural steel ASTM A36; epoxy paint; Fabricate saddles, sleepers per MSS-SP-58; galvanize per ASTM A123
|  | 12.7 | Fit-up & field welding |  |  | Full penetration butt welds; WPS/WPQ per ASME IX; root pass, hot pass, fill & cap passes; preheat when required (PWHT per procedure)
|  | 12.8 | NDT (fabrication & shop) |  |  | Visual 100% (VT); UT/RT sampling depending on class: critical welds 100% RT/UT (manifold & tie-ins), field welds 10–25% RT/UT; MPI/PT per material
|  | 12.9 | Field joint coating | 18" line pipe |  | Heat-shrink sleeve or 3LPE application per manufacturer; DFT 1.8–2.5 mm; holiday detection 100%
|  | 12.1 | Coating QC & inspection | 28" line pipe |  | Coating thickness measurement, adhesion, holiday test; repair per spec
|  | 12.11 | Fabrication of Pigging spools, launcher/receiver supports |  |  | Fabricate per vendor drawing; tolerances ±3 mm; include lifting points
|  | 12.12 | Shop assembly & FAT |  |  | Preassembly of skids/spools where possible; FAT of assemblies (dimensional & pressure test)
|  | 12.13 | Material receipt & MTC verification | 18" line pipe |  | Verify EN 10204 3.1 MTCs for all linepipe, fittings, valves; check heat number, chemical & mechanical test results
|  | 12.14 | Marking, preservation & packing | 18" line pipe |  | Mark components with tag, heat number; preservative oil for short term; seaworthy packing for marine transit; ISO 12944 for preservation
|  | 12.15 | Traceability & documentation | 28" line pipe |  | Weld maps, NDT reports, MTRs, material tags, QA dossiers in EN 10204 format; ISO 9001
C | Construction & Installation
| 1 | Right of Way (RoW) Preparation
|  | 1.1 | Clearing the Right-of-Way (RoW) and grading surface where trench will be dug |  |  | Clearing & grading per approved RoW drawing; clear width per RoW drawing (30 m as per BOD); topsoil strip and stockpile; silt/sediment controls and spill prevention; temporary access mats/ramps where swamp conditions apply; geotechnical pre-checks prior to excavation | Standards cited include: ASME IX / ASME V / ASME B31.8 / API 1102 / ISO 21809 / NACE / EN1997 and project-specific DEP references where you referenced them (DEP 61.40.20.30-Gen and ISO 13847 in your original file). I used BOD / EPC SOW where those documents gave direct requirements (burial depth, padding, hydrotest pressure, coatings, MAOP), and Generic Standards / Best Practice where the documents did not specify method-level values. Field Joint Coating: I specified manufacturer compatibility with factory 3LPE and holiday testing — that prevents coating mismatch failures. HDD: Geotechnical and environmental approvals are mandatory; HDD design must include frac-out mitigation and drilling fluid management plan. Tie-ins: Because of swamp conditions, the tie-ins must ensure lifted ends are out of water prior to welding — this aligns with your earlier context.
|  | 1.2 | Removal of obstacles, vegetation, rocks, and obstructions |  |  | Remove & dispose per Environmental Management Plan (EMP); grub roots and vegetation removed to specified depth; disposal in approved spoil areas; cultural/archaeological finds procedure in place
|  | 1.3 | Temporary access roads, swamp/bog mats, pontoon platforms |  |  | i) Temporary access roads: Geotextile subgrade separation; compacted base ≥ 200 mm; designed for 40-ton haulage; drainage berms & culverts ii) Swamp/bog mats (ROW crossings): Install overlap & pegging, inspection every shift; load rating per equipment iii) Pontoon platforms for work & crew transfer: Deck area modular; gangway with handrails; safe access gangway slope ≤ 1:6; lifejackets & rescue boats on standby
|  | 1.4 | Construction of stringing areas, pipe laydown yards, and temporary camps |  |  | i) Stringing areas: Levelled area, 20–30 m wide, graded ±50 mm; timber/HDPE sleepers for pipe; spacing for welding stations & NDT; erosion controls ii) Pipe laydown yards: Secure fenced compound; hardstanding min. 300 mm compacted base; spacing for 28" and 18" coils/lengths; storage racks/rollers iii) Temporary camps: Accommodation modules (hotel style) 2–4 persons per unit; sanitation, potable water, power generation, medical first aid post; fire escape routes
| 2 | Trenching
|  | 2.1 | Trench depth and width as per design |  |  | Trench depth: nominal cover 1.0–1.2 m; increased cover at roads/crossings as required by local authority; trench width = OD + 0.5–1.0 m working allowance (typical); bedding: 100 mm screened sand; trench side slopes per geotech; dewatering pumps & silt control where water present
| 3 | Pipe Stringing
|  | 3.1 | Transporting and laying out pipes along the RoW |  |  | Stringing: on swamp mats/timber/steel mats; spacing of stringing supports per pipe OD (rollers typically every 2–5 m); use line-up clamps and girth welding stations located on prepared pads; protective wrapping for coating handling; route security during stringing
| 4 | Welding & NDT
|  | 4.1 | Root pass, hot pass, fill and cap welding |  |  | Welding per project WPS/PQR aligned with ASME Section IX and API 1104 for pipeline girth welds; welders qualified per WPS; preheat and PWHT where required per material spec; welding bays with wind breaks for offshore/swamp conditions; reference DEP 61.40.20.30-Gen and ISO 13847:2000 as project practices
|  | 4.2 | Radiographic or ultrasonic testing (RT/UT) |  |  | NDT plan per ITP: 100% visual; RT or UT on root/cap as specified (girth weld acceptance levels per API 1104/ASME V); NDT personnel certified to ISO 9712; NDT records and weld maps maintained
|  | 4.3 | Repair and re-testing of welds |  |  | Repairs per WPS and repair procedure; post-repair NDT (RT/UT) to verify defect removal; rework logs and acceptance per ITP
| 5 | Field Joint Coating
|  | 5.1 | Cleaning joint area |  |  | Surface prep to SSPC-SP10/ISO Sa2.5 for field joints where required; ensure dry, grease-free surface; apply primer per manufacturer instructions prior to FJ sleeve application
|  | 5.2 | Abrasive blasting |  |  | Abrasive blast to Sa2.5 profile; achieve specified anchor profile (e.g., 50–75 µm); DFT checks after curing
|  | 5.3 | Applying joint coating (FBE/3LPE) |  |  | Apply heat-shrink sleeve or liquid epoxy field joint system compatible with factory 3LPE; follow manufacturer cure cycles; conduct holiday detection at 10–15 kV and repair per procedure
| 6 | Lowering-In & Backfilling
|  | 6.1 | Padding |  |  | Sand padding 150 mm under pipe; bedding to be clean washed sand or approved material; padding compaction per spec; avoid contact with trench walls during lowering; no foreign/organic material in bedding
|  | 6.2 | Lowering-in |  |  | Lowering using sidebooms/cranes/barges suited for swamp conditions; follow lowering plan and lifting equipment certs; avoid coating damage — use soft slings and pipe cradles; alignment checks after lowering
|  | 6.3 | Compaction |  |  | Backfill in layers (max 300 mm lifts) and compact where access permits to achieve specified density (e.g., 90% proctor) — compaction testing where applicable; do not overcompact to protect coating
|  | 6.4 | Backfill and reinstatement |  |  | Return excavated material or approved borrow; reinstate topsoil and vegetation where required; erosion control (silt fences, mats); swamp-specific reinstatement to preserve hydrology per EMP
| 7 | Crossings
|  | 7.1 | Road, river, swamp, and utility crossings using HDD or open cut methods |  |  | Primary method HDD for major rivers/roads; HDD entry/exit pits sized per HDD design; minimum host bore diameter ≥1.5× OD; for open cut use cofferdam/dewatering & environmental controls; casing under roads where required – steel casing with min WT per highway load; scour protection and mattressing at water crossings per geotech
| 8 | Block Valve Stations & Pigging Facilities
|  | 8.1 | Valve installation |  |  | Install valves on prepared concrete or steel supports; bolts torqued per flange spec; actuators configured per instrument air/power; provide valve nameplates and isolation capabilities; install local handwheels for maintenance
|  | 8.2 | Valve pits or aboveground supports |  |  | Valve pits to be NEMA/Ingress rated where required; use GRP/HDPE pits for swamp conditions with safe access ladders; where above-ground supports required, use pile foundations or elevated steel supports
|  | 8.3 | Pig launcher/receiver installation |  |  | Launcher/receiver installed on concrete foundation or skid; flange torque and alignment per vendor; local bypass & isolation valves provided; pressure relief & venting arranged to safe location; ensure pig capture and handling area with safe release systems
| 9 | Tie-ins
|  | 9.1 | Tie-in welds between pipeline spreads, manifold outlets, and downstream facilities |  |  | Tie-ins should carried out after lifting of the two pipe string ends out of the water due to the swampy terrain and more than one pup cannot be used at the same tie-in location
|  | 9.2 | NDT, coating, and reinstatement |  |  | All tie-in welds should be 100% NDT and should be coated with heat shrinkable sleeves in accordance with project field joint coating specification
| 10 | Construction Management
|  | 10.1 | QA / QC |  |  | Implement ITPs per discipline, hold points, Material Traceability (EN10204 MTCs), weld records, NDT records; maintain document control in ECM
|  | 10.2 | Development of work methods and procedures |  |  | Method statements, RAMS, lifting plans, welding procedures, crossing method statements and environmental method statements; issuance and approval before execution
|  | 10.3 | Site Supervision |  |  | Qualified site supervisors for each discipline; competency matrix and HSE toolbox talks; reporting lines per EPC organization chart
|  | 10.4 | Logistics |  |  | Logistics plan for swamp transport: barges, sidebooms, matting; spares stock for welding rods, FJ kits, pigging spares; laydown areas and secured storage
|  | 10.5 | Community Cost |  |  | Community engagement plan and compensation payments per ROW agreements and social performance plan
| 11 | Construction Support Facilities
|  | 11.1 | Site Services and Camp Management (welfare, sanitation, transportation, security , communication, plant & equipment maintenace) |  |  | Site camp with accommodation, mess, medical, sanitation; temporary power gensets sized per load study; potable water treatment; fuel bunded storage; waste management per EMP; security & communications (VHF/VSAT)
D | Electrical & Instrumentation
| 1 | AC Mitigation / HV Influence Protection
|  | 1.1 | Supply & installation of high-voltage cable for AC mitigation |  |  | 4-core 90 mm² XLPE-insulated high-voltage mitigation cable, 11 kVA rating, installed in parallel with pipeline; cable sizing based on AC interference modelling per IEEE 80 & NACE SP0177; trench depth, separation distance, and bonding per CP design; all terminations in corrosion-resistant junction boxes
|  | 1.2 | Earthing/grounding for AC interference zones |  |  | Copper-bonded steel grounding rods ≥ 3 m length, driven to low-resistance layer; earthing grid sized per IEEE 80; gradient control mats at high touch-potential zones; bonding to CP system per NACE SP0169; soil resistivity measurements per Wenner 4-pin test
| 2 | Fibre Optic Leak Detection System
|  | 2.1 | Installation of fibre optic cable; one fibre for SCADA/telecom data and one fibre for leak detection |  |  | Dual-purpose Distributed Acoustic Sensing (DAS) fibre optic system; single-mode fibre per ITU-T G.652.D; minimum 48-core armoured fibre; leak detection sensitivity per vendor (>10 m location accuracy); fibre routed along pipeline in FOCC; splice enclosures IP68; integration with SCADA system using OPC-UA or Modbus-TCP.
| 3 | MEI Installation |  |  |  | Installation of instruments, junction boxes, power supply panels, earthing, conduit/cable tray supports; field wiring in armoured XLPE cables per IEC 60502-1/2; hazardous area classification per IEC 60079; instrument hook-up using SS316 tubing; all transmitters SIL-rated per IEC 61508/61511; bonding to CP where required; loop tests per commissioning procedures
| 4 | Lighting system |  |  |  | Lighting poles, supports, cabling, wiring, cable trays, earthing, LED, brackets, anchor bolts, switch gear & control panels
|  | 4.1 | Platform lighting |  |  | For all manifold platforms and access ladders
|  | 4.2 | Area lighting |  |  | For all Pipeline End Facilities
|  | 4.3 | Equipment lighting
|  | 4.4 | Fence/Security lighting
|  | 4.5 | Temporary lighting |  |  | During construction phase for construction camps, welding, coating and stringing areas. Also lighting for night operations.
E | Telecommunication
| 1 | Fibre Optic System
|  | 1.1 | Installation of FOC conduit (FOCC) along pipeline |  |  | Continuous HDPE/ductbank FOCC conduit along pipeline route; minimum inner bore sized to allow 2× 48-core cables (min. 63–110 mm ID duct depending on cable OD); sealed draw-points/hand-holes at max 700 m intervals (splice/joint bays at 3–5 km and at crossings); conduit runs under road crossings in steel casing; draw-points have sealed covers, concrete plinths at PLEM and valve stations; route documentation (chainage coordinates) in as-built | Dual-cable approach: Use two physically separate cables routed in the same or adjacent duct to provide redundancy and to separate SCADA/voice/data traffic from DTS/DAS leak-detection fibre where required by the BOD. DTS/DAS compatibility: If leak detection (DTS/DAS) is required, specify fibre with low backscatter and vendor-validated cable construction for sensing accuracy; coordinate with leak detection vendor on cable type and installation tension limits. Splice bay spacing: Typical industry practice is splice/joint bays every 3–5 km; OTDR launch/receive reels sized to accommodate longest span for accurate testing. Armouring & protection: Use armoured cable and additional mechanical protection (steel casing, concrete covers) at road, rail and river crossings, and close to PLEM/valve stations. Marker posts spacing: Adjust marker spacing to meet local regulations; 250–500 m recommended in accessible corridor, wider spacing may be acceptable in remote swamp areas if documented. ODF & cabinet protection: All ODFs in outdoor cabinets must be lockable, weatherproof (IP66), ventilated as required and bonded to the grounding system. Testing documentation: OTDR traces, power-meter logs, splice logs, and as-built cable schedule must be submitted in both PDF and native OTDR formats and stored in ECM. Safety & segregation: Maintain minimum separation between HV/AC mitigation cables and FO ducts per BOD and local practice; avoid placing FO adjacent to high-EMI sources where possible. Integration: Ensure SCADA comms interface (protocol and redundancy) is defined by BOD; consider ring or dual-route topology where feasible.
|  | 1.2 | Installation of dual 48-core fibre optic cables along pipeline length |  |  | Dual 48-core single-mode fibre optic cables (OS2 / ITU-T G.652.D) — armoured, water-blocked, PE outer sheath, steel tape/armour for mechanical protection; rated for DTS/DAS use where leak detection required. Cable core count and type: 48 cores each; min. tensile strength and crush rating per vendor; temperature range −40°C to +70°C; cable marking with chainage ID every 25 m and unique tag numbers. Install one cable for SCADA/telecom and the second dedicated to leak detection/DTS/DAS (if required)
|  | 1.3 | Testing & commissioning of FOC and FOCC |  |  | OTDR baseline traces for each fibre (pulse settings per span length); end-to-end insertion loss and power meter tests; acceptance criteria per link budget (max total attenuation per span to be defined by comms engineer; typical splice loss ≤ 0.1–0.3 dB; connector loss ≤ 0.5 dB); OTDR trace files stored in ECM; visual inspection of splices and ODF labeling; commissioning report with pass/fail and punch-lists
| 2 | Markers & Posts
|  | 2.1 | Marker posts for fibre optic cable routing |  |  | Marker posts: UV-stabilised HDPE or galvanized steel posts at regular intervals (typical 250–500 m spacing depending on client/regulatory preference); reflective signage with pipeline & telecom warnings; GPS coordinates recorded; special marker posts at road crossings, valve stations, splice bays, and PLEM; posts installed in concrete sockets where required
|  | 2.2 | Measuring posts for signal testing points |  |  | Measuring/test posts (ODF access / OTDR reference points) installed at key chainages and at every splice/ODF location (recommended every 1–2 km); each post houses a small lockable enclosure containing patch panels/ODF, test jumpers, fibre splice log and OTDR launch/receive reels; enclosures rated IP65 for outdoor use and bonded to earthing system; posts labelled with chainage & port numbering
F | Regulatory and Approvals
| 1 | Permits |  |  |  | Obtain all statutory permits: environmental impact approvals (EIA), RoW acquisition permits, swamp access permits, navigation approvals for river crossings, HDD crossing approvals, community entry permits, utility crossing approvals, waste management permits, explosive storage & welding permits. Maintain permit register and renewal schedule
| 2 | Regulatory Approvals | Installation of FOC conduit (FOCC) along pipeline |  |  | Submit telecom permit application for fibre-optic cable routing; secure NCC/Regulator approval for underground telecom infrastructure; comply with national ICT guidelines; provide route maps, cable specs, splice locations and as-built packages to telecom regulator
| 3 | Environmental Fees | Installation of dual 48-core fibre optic cables along pipeline length |  |  | Environmental compliance fees for swamp corridor disturbance, vegetation clearing, hydrology impact mitigation, erosion control, water-body crossing approvals, and waste handling as per Environmental Management Plan (EMP)
| 4 | RoW payments | Testing & commissioning of FOC and FOCC |  |  | Right-of-Way compensation to landowners/communities; temporary occupation fees; crop compensation; reinstatement deposit where applicable; RoW boundary staking and documentation; community engagement according to social responsibility plan
G | Testing, Pre-Commissioning & Commissioning
| 1 | Hydro-testing |  |  |  | Hydrotest procedure per ASME B31.8 & API 1110; Test pressure = 1.5× design pressure (110 barg) = 165 barg; Use calibrated gauges; Do not test against valves—use blind flanges/test heads; Hold test per code; Conduct strength + leak test; Provide HC&A (Hold, Check & Acceptance) reports; Perform pre-test gauging run and cleaning
|  | 1.1 | Hydrotest Water Supply |  |  | Use freshwater/treated swamp water; turbidity <50 NTU; chlorides <500 ppm; pH 6–8; Includes permits, water treatment, disposal plan
|  | 1.2 | Pumping & Containment |  |  | Pumps sized for test pressure 165 barg (1.5 × DP = 110 barg); discharge 50–150 m³/hr
|  | 1.3 | Filling |  |  | Fill at ≤1 m/s; vent high points; remove air pockets
|  | 1.4 | Pressurization |  |  | Ramp-up in 10–20 barg increments; hold at 165 barg for 8 hours
|  | 1.5 | Test Holding |  |  | Monitor pressure drop ≤0.5%
|  | 1.6 | Dewatering |  |  | Use foam/rubber pigs; target dryness <5% humidity
| 2 | Pigging
|  | 2.1 | Cleaning pigs |  |  | High-seal, bi-directional polyurethane disc/brush pigs to remove debris, sand, rust and construction residue; pig train configured per cleanliness requirement; run until debris-free; record launch/receive times; verify passage using pig tracking
|  | 2.2 | Gauging pigs |  |  | Gauging plate (95% ID) mounted on bi-directional pig; aluminum plate preferred; detect dents, ovality, or buckling prior to hydrotest; gauging run acceptance requires no plate deformation
|  | 2.3 | Drying pigs |  |  | Drying via nitrogen/air purge until dew point achieved per BOD (typically ≤ −10°C to −20°C); multiple foam pigs of increasing density; collect dryness log; ensure no residual moisture prior to gas-in
| 3 | Nitrogen Purge & Leak Test
|  | 3.1 | Removal of oxygen and moisture |  |  | Purge with dry nitrogen until oxygen concentration < 2%; dew point ≤ −10°C; nitrogen supplied per ISO 14175 grade N2. Flow velocity & pig train used to sweep remaining pockets; monitor O₂ % at multiple pipeline ends.
|  | 3.2 | Preparation for gas-in |  |  | Leak test with nitrogen to 1.1× operating pressure; soap-test flange joints; verify instrument responses; ensure all valves in correct position; implement ESD functional verification; sign-off punch list prior to gas introduction
| 4 | Consumables for Initial Filling
|  | 4.1 | Lubricants |  |  | Lubricants for valve actuators, seals, and mechanical equipment per vendor datasheets; non-hydrocarbon, temperature-compatible greases; biodegradable options in swamp zones
|  | 4.2 | Chemicals |  |  | Chemicals include biocide, anti-corrosion inhibitor, glycol (if required), odorant (if required pre-commissioning), all sourced to meet ISO/ASTM purity standards
|  | 4.3 | Pipeline internal cleaning agents |  |  | Foam discs, detergents, rust removers certified for hydrocarbon pipeline cleaning; biodegradable agents where required; disposal per EMP
| 5 | Commissioning
|  | 5.1 | Functional checks of valves, instrumentation |  |  | Full loop checks; valve open-close tests; actuator stroke testing; transmitter calibration (4–20 mA/HART); ESD logic functional verification; ensure SIL functions per IEC 61511
|  | 5.2 | Integration with SCADA/telecom |  |  | Communication setup using IEC 60870-5-104/Modbus-TCP/OPC-UA; test alarm points, trending, historian logging; verify FO routing and redundancy; upload configuration backups to ECM
|  | 5.3 | Introduction of gas & handover |  |  | Controlled gas-in sequence: inerted pipeline first, slow pressurization to 10 barg, hold, then stepwise ramp-up to operating pressure; monitor pressure, temperature, leak checks; finalize mechanical completion certificates, commissioning dossiers, punch list closure and handover to operations team
H | HSE, QA/QC, Logistics, Community and Documentation
| 1 | HSE
|  | 1.1 | Permit-to-work system |  |  | Full PTW (Permit-to-Work) system aligned with ISO 45001 & project HSE plan; includes: Hot Work Permits, Cold Work, Confined Space Entry, Lifting Permits, Excavation Permits, Electrical Isolation, Breathing Apparatus requirements, Daily Toolbox Talks, and Job Hazard Analysis (JHA). PTW log to be maintained and audited regularly
|  | 1.2 | Environmental controls |  |  | Environmental Management Plan (EMP) implemented: erosion control, waste segregation, spill prevention, watercourse protection, noise/dust control, vegetation management, swamp hydrology preservation, silt fencing, bunds around fuel tanks; compliance monitoring and reporting
|  | 1.3 | Excavation safety, lifting safety, welding safety |  |  | Excavation safety per OSHA/ISO: shoring or sloping as required; Lifting safety per LOLER/ISO 9927, certified cranes/rigging; Welding safety including fire watch, gas cylinder management, ventilation, FRC PPE, hot work barriers, and H2S awareness; Safety officers must verify daily compliance
|  | 1.4 | Simultaneous Operations (SIMOPS) procedures |  |  | Written SIMOPS plan; identification of conflicting activities; isolation & permit-to-work for concurrent marine and land ops; daily SIMOPS briefings; designated SIMOPS coordinator with stop-work authority
|  | 1.5 | Security management plan (maritime escorts, community liaison guards) |  |  | Maritime escorts for barges (AIS, VHF); community liaison guards (vetting, non-lethal only); security SOPs, incident reporting; 24/7 control room; Duration depends on construction schedule
| 2 | QA/QC
|  | 2.1 | Weld logs |  |  | Maintain weld log with unique weld IDs, welder ID, WPS used, heat numbers, joint type, NDT requirements and results; weld maps linked to chainage; records stored in ECM system
|  | 2.2 | NDT reports |  |  | NDT reports for RT/UT/MT/PT stored with weld traceability; NDT personnel certified ISO 9712 Level II/III; acceptance per API 1104 or ASME Section V (project requirement)
|  | 2.3 | Coating reports |  |  | Field Joint Coating (FJC) logs: surface prep results, DFT readings, holiday test records, batch numbers, cure times; coating inspectors certified to NACE CIP Level I/II or equivalent
|  | 2.4 | Project management & engineering (EPC) |  |  | Typically priced as % of turnkey — to be defined in tender
|  | 2.5 | Insurance |  |  | CAR (Contractor All Risk) insurance; Third-party liability; Worker compensation
|  | 2.6 | Permits & approvals |  |  | ROW, dredging permits, environmental permits, port & marine movement permits; proof of insurance & bonds before MOB
|  | 2.7 | Contingency (technical & schedule) |  |  | Recommend 7.5%–15% depending on risk appetite
|  | 2.8 | Material traceability |  |  | Traceability for line pipe, fittings, flanges, valves, etc., with heat numbers, MTCs per EN 10204 3.1/3.2; maintain storage logs, receiving inspections, and tagging system; all materials must be verified against approved vendor list
| 3 | Logistics & Community
|  | 3.1 | Swamp logistics plan |  |  | Barge scheduling, tide windows, transfer protocols (personnel & cargo), emergency evacuation routes, weather contingency (wind > 25 kn stop ops)
|  | 3.2 | Community engagement and MOU execution support |  |  | Stakeholder mapping; grievance hotline; local content employment targets; written MOUs with local communities; monthly reporting
| 4 | Documentation/Deliverables
|  | 4.1 | As-built drawings |  |  | Develop as-built drawings for pipeline alignment sheets, valve stations, manifolds, crossings (HDD/open cut), FOC routing, CP test posts, and tie-in points; drawings to comply with CAD standards, include chainage references, coordinates, elevations, and approved by engineering before issue
|  | 4.2 | Issued for Construction (IFC) design package |  |  | Full IFC drawings (P&ID, GA, civil, E&I), material take-off, vendor data; checked & stamped by lead discipline; revision control (Rev 0 → Rev X)
|  | 4.3 | Construction workpacks |  |  | Workpack per unit (welding, E&I, civil) with method statement, risk assessment (JSA), hold/witness points, lifting plans, quality checklists
|  | 4.4 | Test packs |  |  | Mechanical completion (MC) and pre-commissioning test packs including: hydrotest records, NDT reports, weld maps, pressure charts, equipment calibration, FJC logs, pigging logs, checklists, punch lists, and verification sheets; formatted per EPC ITP
|  | 4.5 | O&M manuals |  |  | Operation & Maintenance manuals for valves, actuators, instrumentation, CP system, leak detection system, FOC system, pig launchers/receivers, and all rotating equipment. Vendor documentation must include installation, operation, troubleshooting, spare parts list, recommended maintenance and lifespan data
|  | 4.6 | Commissioning dossiers |  |  | Commissioning Dossier includes: checklists, pre-startup safety review (PSSR), functional test sheets, SCADA integration logs, instrument loop checks, nitrogen purge records, leak test reports, red-lined/as-built status, and commissioning certificates; final dossiers structured per project turnover index

## Chklist n Specs - Manifolds
Scope Of Work Checklist & Specifications - Manifolds
Date | 2025-12-15
|  | SYSTEM / SUBSYSTEM |  |  | WORK SCOPE SPECIFICATION
A | Engineering & Design
| 1 | Process & Piping Design
|  | 1.1 | Development of manifold P&IDs, well tie-in configurations, inlet headers, branch lines, bypass loops |  | ASME B31.3 (Process Piping). B31.8 (Gas Transmission & Distribution Piping), API RP 14E for flowline design, Minimum Pipeline Design Pressure = 110 barg
|  | 1.2 | Pressure rating and materials selection based on wet gas composition and upstream reservoir conditions |  | Materials: CS ASTM A106 Gr B / API 5L Gr X70; Pressure Class ANSI 900#; Design Pressure = 110 barg; Corrosion Allowance = 3 mm. Fully Rated to MAOP of 110 barg
|  | 1.3 | Integration with pipeline block valve stations and pigging stations |  | Interfaces designed to ASME B31.8; Launcher/Receiver tie-ins per project pigging philosophy; Design Pressure = 110 barg
| 2 | Structural & Civil Design
|  | 2.1 | Foundations, equipment pads, structural frames, pipe supports |  | Structural steel per ASTM A36/A992; Concrete Grade M30; Load design per Eurocode 3 & 7; Soil bearing capacity per Geotechnical Report
|  | 2.2 | Drainage grading and access layout around manifold station |  | Drainage slope ≥1%; Stormwater handling per project drainage philosophy; Access platform width ≥ 1.2 m
| 3 | Instrumentation & Control Design
|  | 3.1 | Drainage grading and access layout around manifold station |  | Instrument installation per IEC 60079 (hazardous area), IEC 61511 (SIS), and project instrument index
|  | 3.2 | Telemetry and SCADA integration aligning with pipeline monitoring |  | SCADA protocol: Modbus TCP/IP; Interface via RTU; FO backbone per ITU-T G.652; Redundant communication path required
| 4 | Corrosion Protection Design
|  | 4.1 | Internal corrosion control philosophy (chemical injection) |  | Chemical injection rate based on CO₂ & H₂S profile; Corrosion inhibitor per NACE MR0175/ISO 15156; Injection skid sized for 110 barg system
|  | 4.2 | External corrosion protection (coating + CP), coordinated with pipeline cathodic protection |  | Coating: 3LPE per ISO 21809; CP: Impressed Current CP for long-term protection; CP Test Stations per ISO 15589-1
B | Procurement & Fabrication
| 1 | Procurement for ELEP Manifold
|  | 1.1 | Structural / Civil Materials
|  |  | 1.1.1 | Structural steel for manifold platform | Structural Steel: ASTM A36 / ASTM A992; Hot-dip galvanization per ISO 1461; Design loads per Eurocode 3
|  |  | 1.1.2 | Piles & sheet piles | Steel Piles: API 5L Grade B / ASTM A252; Sheet Piles per EN 10248; Coating per ISO 12944
|  |  | 1.1.3 | Gratings, access platforms, stairs, ladders | Gratings: ASTM A36; Stair & Ladder fabrication per OSHA 1910; Slip resistance per ISO 14122
|  |  | 1.1.4 | Pipe Supports / Guides / Anchors | Manufactured per MSS-SP-58/69; Load rating per ASME B31.8 design loads; Hot-dip galvanized
|  | 1.2 | Mechanical Equipment & Materials
|  |  | 1.2.1 | Manifold headers | Pipe: API 5L X70M, WT per design, Design Pressure = 110 barg; Fabrication to ASME B31.8
|  |  | 1.2.2 | PIG Launcher - 28"/32", complete with Closure Door | Design Pressure = 110 barg; Launcher per ASME VIII Div.1; Barrel sizes: 28"/32"; Quick-opening closure per ASME Sec. VIII UG-35
|  |  |  | PIG Receiver - 28"/32", complete with Closure Door | Design Pressure = 110 barg; Launcher per ASME VIII Div.1; Barrel sizes: 28"/32"; Quick-opening closure per ASME Sec. VIII UG-35
|  |  | 1.2.3 | Valves (block valves, MOVs, actuated valves) | API 6D valves; ANSI 900# pressure class; Fire-safe per ISO 10497; Actuators per IEC 61508 SIL-2
|  |  | 1.2.4 | Gas-over-oil actuators | Hydraulic/pneumatic system per API 6DX; Rated for 110 barg pipeline pressure
|  |  | 1.2.5 | Chemical injection system (Corrosion Inhibitor) | Injection skid per NACE MR0175; Pump pressure rating 150 barg; Wetted parts: SS316
|  |  | 1.2.6 | Closed drain vessel, open drain tank, vent stack | Closed drain vessel: 1 m × 3 m T/T, Design Pressure: 7 barg; Open drain tank atmospheric; Vent stack: 7 barg capability
|  |  | 1.2.7 | Gantry crane & jib crane | Crane design per EN 13155; Load capacity (2 tons); Hot-dip galvanized
|  |  | 1.2.8 | Drain, vent, and relief system equipment | Relief valves per API 520/521; Drain/vent piping per ASME B31.8
|  |  | 1.2.9 | Midline slug catcher | Horizontal slug catcher; inlet size 28"; design pressure 110 barg; slug capacity sized per flow (typically 5–10 m³); Includes tie-in spools & drainage
|  |  | 1.2.10 | Tie-in Provision for Biocide Injection | Injection Spool: NPS 1"–2"; MAWP 110 barg (manifold MAOP); SS316L construction; ASME B31.3; ASME B16.5 Isolation Valves: 2 × full-bore valves (double isolation + bleed); API 6D NRVs & Check Valves: Cracking pressure 1–2 bar; SS316L; API 6D/598 Injection Quill: SS316L; anti-siphon design; length ⅓ pipe ID Dosing Pump: 0.1–100 L/hr; accuracy ±1–3%; pressure rating 160 barg; API 675 Skid Piping: SS316L; 600#–900# class; ASME B31.3 Storage Tank: 1–5 m³ methanol/biocide tanks; 110% bund; API 650 Instrumentation: Flow indicator (Coriolis); 4–20 mA; SIL as required; IEC 61511 Heat Tracing: Maintain methanol >5°C; EHT rated for Zone 1; IEC 60079
|  |  | 1.2.11 | Tie-in Provision for Methanol Injection
|  |  | 1.2.12 | Accessories & Bulk Materials - Fittings, Bends, Elbows, Gauges, Isolation joints, Flanges | Flanges: ASME B16.47; Fittings: ASME B16.9; Gaskets: ASME B16.20/B16.21; Isolation joints per EN 10255
|  | 1.3 | Electrical Equipment
|  |  | 1.3.1 | Electrical transformer & electrical room components | Transformer per IEC 60076; IP55 protection; HV/LV panels per IEC 61439
|  |  | 1.3.2 | Power cable supply from Akabel | XLPE armored cable per IEC 60502-1/2
|  |  | 1.3.3 | Earthing system and lightning protection materials | Earthing per IEC 60364; Lightning rods per IEC 62305
|  |  | 1.3.4 | Station lighting, panels, MCC, UPS components | MCC per IEC 61439; UPS per IEC 62040; Area lighting ATEX Zone 1 certified
|  | 1.4 | Instrumentation, Control & Telecom
|  |  | 1.4.1 | RTU / FAR equipment (UPS, panels, battery chargers) | RTU per IEC 61131; UPS per IEC 62040; Battery chargers per IEC 61204
|  |  | 1.4.2 | SCADA system | SCADA protocol Modbus TCP/IP; Interface via FO backbone
|  |  | 1.4.3 | ESD & F&G detection equipment | ESD per IEC 61508 SIL-2; F&G per NFPA 72
|  |  | 1.4.4 | Intrusion detection system | Outdoor-rated sensors per IEC 62676
|  |  | 1.4.5 | Fibre optic equipment + VSAT backup | FO cable per ITU-T G.652; VSAT per ETSI EN 302 340
|  |  | 1.4.6 | Telecom equipment for backbone communication | Industrial-grade telecom per IEC 60870-5
|  |  | 1.4.7 | Field instruments (PT, TT, LT, switches, analyzers) | 4–20 mA/HART; IEC 61511 functional safety
|  |  | 1.4.8 | Check Meter for the ELEP-AKAB Bulk Flow | A Venturi meter with pressure range of 0-110 Barg, instrument range of 0-400 mmscfd, material of construction for wetted parts is Stainless Steel (SS)
|  | 1.5 | Security & Utilities
|  |  | 1.5.1 | High-security fencing | Anti-intrusion fencing per ISO 1794; Height ≥ 2.4 m
|  |  | 1.5.2 | Weather shelter / guard hut | Fabricated per ASTM A36; Roof design per rainfall criteria in BOD
|  |  | 1.5.3 | Mechanical, electrical, civil bulk materials | General M,E&C materials per project approved vendor list
| 2 | Fabrication for ELEP Manifold
|  | 2.1 | Structural platform steel fabrication |  | Fabrication per AWS D1.1; Coating per ISO 12944
|  | 2.2 | Fabrication of headers, manifold spools & interconnection piping |  | Fabrication per ASME B31.8; NDT per ISO 17638/17640
|  | 2.3 | Prefabrication of launcher and receiver piping spools |  | Weld procedures per ISO 15614; Dimensional tolerances per ASME VIII
|  | 2.4 | Fabrication of pipe supports, cable tray supports, racks |  | Fabrication per MSS-SP-58; Structural steel per ASTM A36
|  | 2.5 | FAR / RTU container support frames |  | Structural fabrication per EN 1090
|  | 2.6 | Skid frames for chemical injection unit |  | Skid fabrication per ASME IX; Weatherproof coating ISO 12944
|  | 2.7 | Fabrication of access structures (ladders, platforms, walkways) |  | Fabrication per ISO 14122; Anti-slip gratings per ASTM A36
|  | 2.8 | Surface preparation & painting |  | Blast cleaning SA 2.5 per ISO 8501; Painting per ISO 12944 C4/C5
|  | 2.9 | Welding, NDT, coating of prefabricated components |  | Weld NDT per ISO 9712; Coating per ISO 21809
| 3 | Procurement for AKAB Manifold
|  | 3.1 | Structural / Civil
|  |  | 3.1.1 | Structural steel for pig receiver platform | Structural Steel: ASTM A36 / ASTM A992; Galvanization per ISO 1461; Load design per Eurocode 3
|  |  | 3.1.2 | Piles & sheet piles for foundations | Steel piles per API 5L grade B / ASTM A252; Sheet piles per EN 10248; Coating per ISO 12944
|  |  | 3.1.3 | Stairways, handrails, access platforms | Fabricated per ISO 14122; Slip-resistant grating per ASTM A36
|  | 3.2 | Mechanical Equipment & Materials
|  |  | 3.2.1 | PIG Receiver - 28"/32", complete with Closure Door | ASME B31.8; Design Pressure 110 barg; Closure per ASME VIII UG-35; Barrel size 28"/32"
|  |  | 3.2.2 | Pig handling trolley/guide systems | Load design per EN 13155; Stainless Steel SS304 frame
|  |  | 3.2.3 | Valves & piping for pig receiver | API 6D Valves, ANSI 900#; Piping API 5L X70; Branch connections per ASME B31.8
|  |  | 3.2.4 | Jib crane for pig handling | SWL 1–5 tons; Design per EN 13001; Hot-dip galvanized
|  |  | 3.2.5 | Open drain tank | Atmospheric pressure; Min size 2m × 1m × 1m; Welded per ASME VIII for atmospheric vessels
|  |  | 3.2.6 | Depressurization piping (tie-in to GPP flare system) | API 5L carbon steel; Tie-in to GPP flare; Pressure rating ANSI 900#
|  |  | 3.2.7 | Earthing system materials | IEC 60364 earthing grid; Copper-bonded rods
|  |  | 3.2.8 | Accessories & Bulk Materials - Fittings, Bends, Elbows, Gauges, Isolation joints, Flanges | Flanges ASME B16.47; Fittings ASME B16.9/11; Gaskets ASME B16.20/21; Isolation joints EN 10255
|  | 3.3 | Electrical
|  |  | 3.3.1 | Lighting system, small power, local distribution board | Lighting ATEX Zone 1; Cable per IEC 60502-1; Panel boards per IEC 61439
|  |  | 3.3.2 | Earthing & bonding materials | Earth grid per IEC 60364; Lightning protection per IEC 62305
|  | 3.4 | Instrumentation, Control & Telecom
|  |  | 3.4.1 | Instrumentation for pig receiver operation | Transmitters: 4–20mA/HART; SIL-2 per IEC 61511
|  |  | 3.4.2 | Pressure & temperature instruments | PT/TT per IEC 60770-1; Accuracy ±0.1%
|  |  | 3.4.3 | RTU termination hardware | RTU wiring per IEC 61158; Surge protection per IEC 61643
|  |  | 3.4.4 | Fibre optic cable termination hardware | FO per ITU-T G.652; OFDF per IEC 61753
|  |  | 3.4.5 | SCADA interfaces | Modbus TCP/IP; Redundant FO paths
|  |  | 3.4.6 | Mechanical, electrical, civil bulk materials | General M,E&C materials per project approved vendor list
| 4 | Fabrication for AKAB Manifold
|  | 4.1 | Fabrication of structural platform modules |  | Fabrication per AWS D1.1; Coating ISO 12944
|  | 4.2 | Fabrication of supports for PIG Receiver & Receiver piping |  | ASME B31.8; Pipe supports MSS-SP-58
|  | 4.3 | Prefabrication of piping spools for the receiver |  | ASME IX welding; NDT per ISO 17640
|  | 4.4 | Fabrication of ladder, platform, handrail structures |  | ISO 14122; Hot-dip galvanized
|  | 4.5 | Fabrication of jib crane mounting frames |  | EN 13155; Structural steel ASTM A36
|  | 4.6 | Fabrication of drain tank support structures |  | ASME VIII; Support steel ASTM A36
|  | 4.7 | Coating, blasting & painting |  | SA 2.5 per ISO 8501; Coating ISO 12944 C4/C5
|  | 4.8 | Shop welding, test assembly, alignment trials |  | Weld procedures per ISO 15614; Fit-up checks per ASME V
| 5 | Procurements for BBOU Manifold
|  | 5.1 | Structural / Civil Materials
|  |  | 5.1.1 | Structural steel for platform superstructure | ASTM A36/A992; Hot-dip galvanized ISO 1461
|  |  | 5.1.2 | Piles and sheet piles for foundation | API 5L Gr B / ASTM A252; Sheet piles EN 10248
|  |  | 5.1.3 | Gratings, handrails, ladders, platforms | ISO 14122; Steel ASTM A36
|  | 5.2 | Mechanical Equipment & Materials
|  |  | 5.2.1 | Field Manifold headers | API 5L X70, WT per stress calculations; ASME B31.8
|  |  | 5.2.2 | PIG Launcher - 18"/22", complete with Closure Door | Design Pressure 110 barg; ASME VIII closure; 18"/22" barrels
|  |  | 5.2.3 | PIG LReceiver - 18"/22", complete with Closure Door | Design Pressure 110 barg; ASME VIII closure; 18"/22" barrels
|  |  | 5.2.4 | Valves (block valves, MOVs, actuated valves) | API 6D; ANSI 900#; Fire-safe ISO 10497
|  |  | 5.2.5 | Gas-over-oil actuators | API 6DX; SIL-2 rated
|  |  | 5.2.6 | Chemical injection skid & accessories (corrosion inhibitor) | NACE MR0175; SS316 wetted parts
|  |  | 5.2.7 | Closed drain vessel and open drain tank | Closed drain: 1m x 3m T/T, 7 barg; Open drain: atmospheric
|  |  | 5.2.8 | Gantry crane & jib crane | Crane design per EN 13155; Load capacity (2 tons); Hot-dip galvanized
|  |  | 5.2.9 | Vent stack | 7 barg design; SS316 or CS+coating ISO 12944
|  |  | 5.2.10 | Navigation aid equipment | ATEX-certified; Marine-grade per IALA
|  |  | 5.2.11 | Tie-in Provision for Biocide Injection | Injection Spool: NPS 1"–2"; MAWP 110 barg (manifold MAOP); SS316L construction; ASME B31.3; ASME B16.5 Isolation Valves: 2 × full-bore valves (double isolation + bleed); API 6D NRVs & Check Valves: Cracking pressure 1–2 bar; SS316L; API 6D/598 Injection Quill: SS316L; anti-siphon design; length ⅓ pipe ID Dosing Pump: 0.1–100 L/hr; accuracy ±1–3%; pressure rating 160 barg; API 675 Skid Piping: SS316L; 600#–900# class; ASME B31.3 Storage Tank: 1–5 m³ methanol/biocide tanks; 110% bund; API 650 Instrumentation: Flow indicator (Coriolis); 4–20 mA; SIL as required; IEC 61511 Heat Tracing: Maintain methanol >5°C; EHT rated for Zone 1; IEC 60079
|  |  | 5.2.12 | Tie-in Provision for Methanol Injection
|  |  | 5.2.13 | Accessories & Bulk Materials - Fittings, Bends, Elbows, Gauges, Isolation joints, Flanges | ASME B16.47, B16.9, B16.11; Gaskets B16.20/21
|  | 5.3 | Electrical Equipment
|  |  | 5.3.1 | Electrical transformer | IEC 60076; IP55
|  |  | 5.3.2 | Power supply cable from Akabel | XLPE per IEC 60502
|  |  | 5.3.3 | Solar power backup system | PV IEC 61215; Inverter IEC 62116
|  |  | 5.3.4 | Electrical room components | HVAC per ASHRAE; Panels per IEC 61439
|  |  | 5.3.5 | Earthing & lightning protection materials | IEC 62305, IEC 60364
|  |  | 5.3.6 | Lighting system and electrical panels | ATEX Zone 1 luminaires; Cables IEC 60502
|  | 5.4 | Instrumentation, Control & Telecom
|  |  | 5.4.1 | RTU / Control Room equipment (UPS, batteries, panels) | IEC 61131; UPS IEC 62040
|  |  | 5.4.2 | Field Auxiliary Room (FAR) enclosure & components | IP66 certified; Fire-rated enclosure
|  |  | 5.4.3 | SCADA, PLC/RTU, ESD system | SIL-2 IEC 61508; Modbus TCP/IP
|  |  | 5.4.4 | F&G detection system | NFPA 72; IEC 60079 for ATEX
|  |  | 5.4.5 | Intrusion detection system | IEC 62676
|  |  | 5.4.6 | Fibre optic equipment + VSAT backup | FO ITU-T G.652; VSAT ETSI EN 302
|  |  | 5.4.7 | Field instruments (pressure, temperature, flow transmitters) | 4–20 mA/HART; IEC 61511
|  |  | 5.4.8 | Check Meter for the BBOU-ELEP Bulk Flow | A Venturi meter with pressure range of 0-110 Barg, instrument range of 0-400 mmscfd, material of construction for wetted parts is Stainless Steel (SS)
|  | 5.5 | Security, Safety & Miscellaneous
|  |  | 5.5.1 | High-security fencing | ISO 1794 anti-intrusion; Height ≥ 2.4 m
|  |  | 5.5.2 | Weather shelter / guard hut | Steel ASTM A36; Roofing per BOD rainfall spec
|  |  | 5.5.3 | Cable trays, supports, junction boxes | Cable trays NEMA VE2; JB IP66
|  |  | 5.5.4 | Mechanical, electrical, civil bulk materials | General M,E&C materials per project approved vendor list
| 6 | Fabrication for BBOU Manifold
|  | 6.1 | Fabrication of structural platform elements (beams, frames, skids) |  | AWS D1.1; Hot-dip galvanized ISO 1461
|  | 6.2 | Fabrication of supports, pipe racks, pipe sleepers, brackets |  | MSS-SP-58/69; ASME B31.8 loads
|  | 6.3 | Pre-fabrication of manifold headers & interconnecting spools |  | Fabrication per ASME B31.8; Weld NDT per ISO 17640
|  | 6.4 | Prefabrication of launcher and receiver piping spools |  | ASME IX procedures; Dimensional per ASME VIII
|  | 6.5 | Fabrication of crane platforms and mounting structures |  | EN 13155; ASTM A36 Steel
|  | 6.6 | Fabrication of auxiliary structures (chemical injection skid frame, FAR foundation steel) |  | ISO 12944 coating; ASME IX welds
|  | 6.7 | Fabrication of drain vessels support frames, vent stack base |  | ASME VIII; Structural per EN 1090
|  | 6.8 | Coating, blasting, painting of all fabricated steel |  | ISO 8501 SA 2.5; ISO 12944 C4/C5
|  | 6.9 | Shop welding, testing, trial fit-up prior to transport |  | ISO 15614 WPS; Fit-up per ASME V
| 7 | Vendor Testing
|  | 7.1 | Valve FAT, actuator FAT, manifold skid FAT. |  | FAT per API 6D (valves), API 6DX (actuators), IEC 61439 (panels)
C | Construction & Installation
| 1 | Civil Works- All Manifolds Foundation
|  | 1.1 | Site clearing, leveling and foundation construction |  | Clearing per ISO 11093; Compaction to 95% Modified Proctor; Foundation leveling tolerance ±10 mm
|  | 1.2 | Mobilization & Demobilization of resources (Personnel, Equipment & Materials), inclusive of accommodation, marine logistics and work barges for duration of works |  | Marine logistics per project marine plan; Construction duration 8 months (EPC requirement)
|  | 1.3 | Fabricate to be used as pile casing CS pipe |  | Pipe Grade: API 5L Grade B; Length 4300 m total; OD=406mm; Wall thickness per design
|  | 1.4 | Drill cased pile to depth of 50m |  | Drilling per API RP 2A; Min pile penetration 50m; 2 piles per cap (in 43 places)
|  | 1.5 | Concrete infill for the cased pile |  | M30 concrete; Required volume 559 m³ +10%; Placement per ACI 304
|  | 1.6 | Concrete works for both pile cap |  | M30 reinforced concrete; Cap size 2m × 2m × 0.9m; Reinforcement per BS 8110
|  | 1.7 | Reinforcing steel bars to pile cap, cased pile & spread foundations |  | Steel grade: B500B; Quantities: 100–150 kg/m³ depending on element
|  | 1.8 | Formwork to pile caps |  | Timber/steel formwork per EN 12812; Dimensions L=2m, B=2m, H=0.9m
|  | 1.9 | Carry out static pile load test |  | Test per ASTM D1143; Safety factor ≥2
| 2 | Structural Steel Works- All Manifolds Platform
|  | 2.1 | Steel columns serving as Primary frames |  | Steel ASTM A36/A992; Fabrication per AWS D1.1; Coating ISO 12944 C4/C5
|  | 2.2 | Steel columns serving as Secondary frames |  | Steel ASTM A36/A992; Fabrication per AWS D1.1; Coating ISO 12944 C4/C5. Load combinations per Eurocode 3
|  | 2.3 | Provision for Shortfall / Un-modelled members (Bolt & nuts, Gusset Plates, Stiffners, Bracings etc) |  | Bolts: ASTM A325; Gussets per EN 1993-1; Stiffeners 6–10 mm plates
|  | 2.4 | HD grating for platform |  | Heavy-duty grating per ISO 14122; 30×5 mm serrated bars; Galvanized ISO 1461
| 3 | Mechanical Installation- ELEP Manifold
|  | 3.1 | Installation of manifold headers and interconnection piping |  | Install per ASME B31.8; Field welds per ASME IX; Alignment tolerance ±3 mm
|  | 3.2 | Installation of pig launcher/receiver assembly |  | Launcher/Receiver installed per manufacturer specs; Quick-opening closure per ASME UG-35
|  | 3.3 | Mounting and alignment of valves, actuators, and spools |  | API 6D valves; Actuator alignment tolerance ±1 mm; Bolt torquing per ASME PCC-1
|  | 3.4 | Torque tightening of flange joints |  | Torque per ASME PCC-1 guidelines; Flanges ASME B16.5/47
|  | 3.5 | Installation of drains, vents, strainers, and auxiliary equipment |  | Drain/vent sizes per P&ID; Strainers per API RP 14E
|  | 3.6 | Field welding and dimensional verification |  | Weld NDT: 100% visual + RT/UT per ISO 17640; Dimensional per ASME B31.8
| 4 | Mechanical Installation- AKAB Manifold
|  | 4.1 | Installation of pig receiver barrel and quick-opening closure |  | Receiver installation per ASME VIII Div.1; Closure per ASME UG-35
|  | 4.2 | Connection of kicker line, bypass piping, inlet/outlet spools |  | Piping API 5L X70; Welds ASME IX; Fit-up per ASME B31.8
|  | 4.3 | Installation of valves, actuators, strainers, vents, drains |  | API 6D valves; Strainers per ISO 9001 design spec
|  | 4.4 | Torqueing of flanged joints |  | Bolting per ASME PCC-1; Gaskets per ASME B16.20/21
|  | 4.5 | Field welding, dimension verification, alignment checks |  | Weld NDT per ISO 9712; Alignment tolerance ±3 mm
| 5 | Mechanical Installation- BBOU Manifold
|  | 5.1 | Installation of manifold headers, spools, and tie-in piping to pipelines |  | API 5L X70; Stress checks per ASME B31.8; Tie-ins hydrotested per API 1110
|  | 5.2 | Installation of pig launcher assembly |  | Launcher per ASME VIII; 18"/22" barrels; Closure per UG-35
|  | 5.3 | Alignment and securing of valves and actuators |  | API 6D; SIL-2 actuator integration per IEC 61511
|  | 5.4 | Installation of drain drums, open drain tanks, vent stacks |  | Tanks per ASME VIII; Stack design 7 barg; Coating ISO 12944 C5
|  | 5.5 | Installation of mechanical supports and anchor blocks |  | Supports per MSS-SP-58; Anchors per EN 1993
|  | 5.6 | Torqueing of flange bolts |  | ASME PCC-1 torque table
|  | 5.7 | Field welding, grinding, and dimensional checks |  | Weld procedures ASME IX; Dimensional tolerance ±3 mm
| 6 | Site Finishing
|  | 6.1 | Fencing, access roads, drainage, lighting |  | Fencing ISO 1794; Access road compaction 95% MDD; Drainage slope ≥1%; Lighting ATEX Zone 1
D | Electrical & Instrumentation
| 1 | Electrical Scope for ELEP Manifold | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 1.1 | Power & Distribution
|  |  | 1.1.1 | Installation of LV power cables and isolating devices | LV cables per IEC 60502-1; Cable routing per IEC 60364; Isolation devices per IEC 60947-3
|  |  | 1.1.2 | Mounting of electrical panels, junction boxes, and lighting circuits | Panels per IEC 61439; JB IP66; Lighting wiring per IEC 60364-7-712
|  |  | 1.1.3 | Cable termination | Termination lugs per IEC 61238-1; Glanding per IEC 62444
|  | 1.2 | Earthing & Lightning Protection
|  |  | 1.2.1 | Installation of earth electrodes and earthing grid | Earthing grid per IEEE 80; Rods: Copper-bonded steel; Earth resistance <1 Ω
|  |  | 1.2.2 | Bonding of equipment, platform steel, valves, actuators | Bonding conductors per IEC 60364-5-54; Ex-rated bonding for hazardous areas
|  |  | 1.2.3 | Lightning protection installation | Lightning protection per IEC 62305 (LPS Level IV)
|  | 1.3 | Lighting System
|  |  | 1.3.1 | Installation of general lighting | ATEX Zone 1/2 luminaires per IEC 60079-7; Photometric performance per IES LM-79
|  |  | 1.3.2 | Routing of lighting cables, conduits, and cable trays | Cable trays per NEMA VE-1/VE-2; Conduits per IEC 61386
|  |  | 1.3.3 | Testing and energization | Electrical testing per IEC 60364-6; Megger test at 500/1000 V
| 2 | Instrumentation Scope for ELEP Manifold | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 2.1 | Field Instrumentation
|  |  | 2.1.1 | Installation of transmitters (PT, TT, LT, FT) and local gauges | Transmitters: 4–20 mA/HART; Accuracy ±0.1%; Enclosures IP66; ATEX Zone 1
|  |  | 2.1.2 | Installation of control valves, actuators, positioners | Control valves per IEC 60534; Actuators per IEC 61508 SIL-2
|  |  | 2.1.3 | Installation of instrument manifolds, impulse lines, tubing | SS316 tubing per ASTM A213; Manifolds per ANSI/ISA 75.08.02
|  | 2.2 | Control & Safety Systems
|  |  | 2.2.1 | Installation of RTU equipment, I/O modules, and interface cables | RTU per IEC 61131; I/O per IEC 61158; Surge protection per IEC 61643
|  |  | 2.2.2 | Installation of ESD pushbuttons and interlock systems | ESD SIL-2 per IEC 61511; Pushbuttons per IEC 60947-5-1
|  |  | 2.2.3 | Installation of F&G detectors and testing devices | Gas detectors per IEC 60079-29; Flame detectors per EN 54-10
|  | 2.3 | Instrument Cabling
|  |  | 2.3.1 | Pulling, laying, glanding, and termination of instrument cables | Cables IEC 60092-376; Glands per IEC 62444
|  |  | 2.3.2 | Installation of instrument junction boxes | JB IP66/Ex-e rated; IEC 60079-7
|  |  | 2.3.3 | Cable tray installation for instrument routes | Cable trays per NEMA VE2; Corrosion class ISO 12944
| 3 | Electrical Scope for AKAB Manifold | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 3.1 | Power Installation
|  |  | 3.1.1 | Installation of LV cables powering control devices and indicators | LV cables per IEC 60502-1; Segregation per IEC 60364-5-52
|  |  | 3.1.2 | Installation of junction boxes and cable trays | JB IP66; Cable trays NEMA VE-2
|  |  | 3.1.3 | Cable termination | Terminations per IEC 61238; Glands per IEC 62444
|  | 3.2 | Earthing System
|  |  | 3.2.1 | Installation of earth rods and earthing grid | Earth grid per IEEE 80; Rods copper-bonded; <1 Ω
|  |  | 3.2.2 | Bonding of pig receiver, valves, actuators, steel platform | Bonding per IEC 60364-5-54
|  |  | 3.2.3 | Earth continuity testing and certification | Testing per IEC 60364-6
|  | 3.3 | Lighting System
|  |  | 3.3.1 | Installation of adequate lighting around pig receiver platform | ATEX Zone 1/2 luminaires; Mounting height ≥2.3 m
|  |  | 3.3.2 | Routing and termination of lighting cables | IEC 60364 wiring rules
|  |  | 3.3.3 | Testing and energization | IEC 60364-6
| 4 | Instrumentation Scope for AKAB Manifold | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 4.1 | Field Instrumentation
|  |  | 4.1.1 | Installation of transmitters (PT, TT, LT, FT) and local gauges | Accuracy ±0.1%; HART-enabled; SS316 wetted parts
|  |  | 4.1.2 | Installation of actuator feedback instruments and limit switches | Position feedback per NAMUR NE43
|  |  | 4.1.3 | Tubing installation, impulse line routing, bracket mounting | SS316 tubing; Installation per ISA RP7.1
|  | 4.2 | Integration with Control Systems
|  |  | 4.2.1 | Wiring of field instruments to RTU | Modbus/4–20 mA; Shielding & grounding per IEC 60364
|  |  | 4.2.2 | Integration of pig receiver status signals (open/close) | ESD logic per IEC 61508 SIL-2
|  |  | 4.2.3 | ESD pushbutton and shutdown signal wiring | IEC 60947-5-1, SIL-2
|  | 4.3 | Calibration & Setup
|  |  | 4.3.1 | Calibration of all instruments | Calibration per ISA S51.1; Cert traceable to ISO 17025
|  |  | 4.3.2 | Verification of zero/span, linearity, and accuracy | As per manufacturer datasheet; IEC 61298
|  |  | 4.3.3 | Labeling and tagging | Tag plates SS316; ISO 14617 symbols
| 5 | Electrical Scope for BBOU Manifold | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 5.1 | Power & Distribution
|  |  | 5.1.1 | Installation of power supply cables routed from Akabel station | XLPE cables; Voltage drop ≤3%; Conductor size per load calc
|  |  | 5.1.2 | Termination of power cables, installation of junction boxes and distribution panels | IEC 61238; Cable glands per IEC 62444
|  |  | 5.1.3 | Installation of small-power outlets and isolation devices | IEC 60364-7-707 requirements
|  | 5.2 | Earthing System
|  |  | 5.2.1 | Installation of complete earthing system consisting of earth rods, grid, and bonding | IEC 60364-5-54
|  |  | 5.2.2 | Earthing of all metallic structures, valves, instruments and equipment | Low-resistance bonding <0.1 Ω
|  |  | 5.2.3 | Lightning protection installation | IEC 62305 LPS-IV
|  | 5.3 | Lighting System
|  |  | 5.3.1 | Installation of area lighting, cable trays, conduits | ATEX Z1 luminaires; NEMA VE-2 trays
|  |  | 5.3.2 | Functional checks and energization of lighting circuits | IEC 60364-6 testing
| 6 | Instrumentation Scope for BBOU Manifold | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 6.1 | Field Instrumentation
|  |  | 6.1.1 | Installation of transmitters (PT, TT, LT, FT) and local gauges | Accuracy ±0.1%; SS316; HART
|  |  | 6.1.2 | Mounting and alignment of valve actuators | SIL-2 actuator requirements per IEC 61508
|  |  | 6.1.3 | Installation of instrument tubing, fittings, impulse lines | SS316; Installation per ISA RP7.1
|  | 6.2 | Control System Integration
|  |  | 6.2.1 | Installation of RTU panel and associated equipment | IEC 61131; IP65; FO link to SCADA
|  |  | 6.2.2 | Wiring of all signals (AI, AO, DI, DO) from field instruments to RTU | IEC 60364; Shielded instrumentation cable
|  |  | 6.2.3 | Integration of MOVs, actuators, and interlock systems | SIL-2 per IEC 61511
|  | 6.3 | Safety Instrumented Systems
|  |  | 6.3.1 | Installation of ESD pushbuttons and logic modules | IEC 60947-5-1; SIL-2
|  |  | 6.3.2 | Installation of F&G detectors and alarm beacons | Gas: IEC 60079-29; Flame: EN 54-10
|  |  | 6.3.3 | Calibration and verification of all instruments | ISO 17025 traceability
| 7 | Power Distribution | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 7.1 | Power cabling, routing, termination |  | Panel per IEC 61439; EHT cables per IEC 60800
|  | 7.2 | Power distribution boards
| 8 | Heat Tracing | Installation of fibre optic cable; one fibre for SCADA/telecom data and one fibre for leak detection
|  | 8.1 | Electrical heat tracing for process piping, including: power distribution panel, cabling, interconnection and termination |  | Electrical heat tracing per IEEE 515; ATEX-certified; Maintain temp 5–20°C above ambient
| 9 | Solar Power |  |  | PV modules per IEC 61215; Inverters per IEC 62116; Batteries per IEC 62619
E | Telecommunication
| 1 | Telecommunication Scope for All Manifolds | Supply & installation of 4-core 90 mm² x 11 kVA high-voltage cable for AC mitigation
|  | 1.1 | Fibre Optic Backbone
|  |  | 1.1.1 | Routing of FOC from Manifold to telecom interface point (for ELEP & AKAB) and from pipeline network into manifold (for BBOU only) | Single-mode FO cable, OS2 type, ITU-T G.652D, UV-resistant PE sheath; burial depth 1.0–1.2 m in ROW; min. bend radius ≥ 20 × cable OD
|  |  | 1.1.2 | Termination into ODF panel | ODF termination using SC/APC connectors, IL ≤ 0.3 dB, RL ≥ 60 dB; ODF rack per IEC 61753-1
|  |  | 1.1.3 | FO splicing and integrity testing | Fusion splicing (loss ≤ 0.1 dB per splice); OTDR testing at 1310/1550 nm per IEC 61280-4-2
|  | 1.2 | SCADA Communication
|  |  | 1.2.1 | Connection of RTU to SCADA network through FO link | RTU–SCADA link via single-mode FO; Ethernet 100/1000BASE-LX; redundancy per IEC 62443
|  |  | 1.2.2 | Verification of SCADA communication signals | Modbus TCP/IP or DNP3 protocol verification; packet loss ≤ 1%; latency < 50 ms
|  |  | 1.2.3 | Alarm signal validation | End-to-end validation with RTU polling cycle ≤ 2 sec; alarm verification per ISA 18.2
|  | 1.3 | Communication Systems
|  |  | 1.3.1 | Telecom racks and in-cabinet equipment | 19-inch racks per IEC 60297; grounding per IEEE Std 1100; climate-controlled telecom enclosure
|  |  | 1.3.2 | Integration with control room systems | Ethernet-based integration using fibre patch panels, VLAN segmentation, cybersecurity per IEC 62443
|  | 1.4 | CCTV & Security
|  |  | 1.4.1 | CCTV cameras & networking | IP CCTV cameras, ONVIF-compliant; POE supply; minimum resolution 1080p; NVR storage ≥ 30 days; network per IEEE 802.3
F | Testing, Pre-Commissioning & Commissioning
| 1 | Hydrotest / Pneumatic Test |  |  | Hydrotest per ASME B31.8/B31.3 at 1.5 × design pressure; pneumatic test only where hydrotest is not feasible, per ASME Sec VIII Div.1 (max 1.1 × design pressure). Test medium: filtered water; hold time ≥ 4 hrs; acceptance based on pressure stability and zero visible leakage
| 2 | Instrument Loop Checks |  |  | Verification of each field instrument loop from sensor → junction box → marshalling → RTU/PLC; continuity, polarity, range, calibration, logic confirmation, per ISA 5.1 & ISA S18.2
| 3 | ESD and Control System Testing |  |  | Verification of shutdown logic, cause & effect testing (C&E matrices), emergency trip signals, interlocks, system redundancy, per IEC 61511 (SIS standard)
| 4 | Functional Testing of Valves and Instruments |  |  | Stroke testing of MOVs, ESD valves, calibration verification of PT/TT/LT/FT transmitters, actuator torque verification, leak testing per API 598 for valves
| 5 | Flushing and cleaning of lines |  |  | Mechanical cleaning using compressed air / nitrogen blow-through; flushing velocity ≥ 3 m/s; pigging for debris removal; cleanliness verification per API RP 1110
| 6 | Energization of electrical systems and lighting circuit verification |  |  | Pre-energization tests: insulation resistance (IR) test per IEEE 400, continuity tests, polarity checks, earth resistance ≤ 1 Ω, breaker functionality, lighting lux-level verification
| 7 | Instrument calibration checks and full loop verification |  |  | Zero/span calibration, linearity checks, pressure/temperature calibration with certified standards (ISO 17025), loop testing end-to-end before commissioning
| 8 | RTU communication checks and SCADA data validation |  |  | Validation of RTU polling cycle, data accuracy, alarm/command signals, FO link integrity, network redundancy tests per IEC 61850 & DNP3 protocol testing
| 9 | Introduction of Live Gas and Commissioning |  |  | Gas-in procedure per EPC SOW: inerting/purging with nitrogen, controlled pressurization in steps (25% → 50% → 100%), leak checks, structural integrity verification before handover
| 10 | Functional System Commissioning |  |  | Validation of complete manifold operation: valves, ESD systems, communication, instrumentation, electrical loads, F&G systems, integration with pipeline SCADA
G | HSE, QA/QC, and Documentation
| 1 | HSE
|  | 1.1 | HSE Standards & Compliance (Health, Safety & Environment requirements, Safety regulations, Site safety management) |  | Compliance with Nigeria HSE Regulations, DPR/NUIMS guidelines, NFPA site safety requirements, ISO 45001 safety management, confined space & hot-work controls, permit-to-work (PTW), job safety analysis (JSA)
|  | 1.2 | Risk Assessments & Method Statements (Job Hazard Analysis (JHA), Method statements, Safe execution procedures) |  | Mandatory Job Hazard Analysis (JHA), Method Statements for lifting, welding, excavation, radiography, chemical handling; risk level classification per ISO 31000
|  | 1.3 | Emergency Response & Safety Controls (Fire & Gas systems, ESD logic, Safety Control Systems) |  | Implementation of ESD logic; fire extinguishing readiness, muster points, gas detection alarms (F&G), emergency evacuation plan per NFPA 72 & NFPA 59A for gas facilities
|  | 1.4 | HSE During Construction (safe execution of Excavation, Lifting, Welding, Trenching, Coating & Installation works) |  | Work-at-height compliance, trenching shoring protection (OSHA 1926), lifting plans, welding & hot work controls, environmental controls (spill prevention, noise, emissions)
| 2 | QA/QC
|  | 2.1 | Quality Control & Inspection Requirements ( For welding, NDT, coating, installation) |  | QC covering welding, NDT, fabrication tolerances, coating inspection, bolt torqueing, alignment checks; QC per ISO 9001, ASME B31.3/B31.8, and API 1104 welding acceptance
|  | 2.2 | Welding, Coating, Material Traceability |  | Welding per ASME IX; Material Test Certificates (MTCs) to EN 10204 3.1; coating inspection per ISO 12944 & NACE standards; traceability records for all tagged equipment
|  | 2.3 | Factory Acceptance Tests (FATs) (for Valves, Actuators, Electrical panels, Instrumentation panels) |  | FAT for valves/actuators, electrical and instrumentation panels; functional testing per IEC 61439 for electrical panels and API 6D / API 598 for valves
|  | 2.4 | Hydrotesting & Pressure Testing Requirements (Manifold headers, Branch lines, Tie-in spools) |  | Pressure testing of manifold headers, tie-in spools, drains/vents at 1.5 × design pressure (hydrotest) per ASME B31.3/B31.8; pneumatic test only where hydrotest is not feasible
| 3 | Documentation/Deliverables
|  | 3.1 | As-built drawings |  | As-built drawings for civil, structural, piping, E&I, mechanical, telecom; prepared in AutoCAD or MicroStation per project drafting standard; final submission in native + PDF
|  | 3.2 | Test Reports & Inspection Records (includes NDT reports, Coating reports, Welding logs, Hydrotest packages, QC dossiers) |  | Complete dossier including NDT reports (UT, RT, MT, PT), coating logs, welding maps, hydrotest packs, instrument calibration sheets, electrical test sheets (IR test, continuity)
|  | 3.3 | Commissioning & Handover Documents ( It requires Commissioning reports, Pre-commissioning documents, Test certificates, Handover dossiers) |  | Pre-commissioning reports, commissioning certificates, SAT/FAT reports, ESD logic test results, SCADA communication logs, punch list closure packages
|  | 3.4 | Vendor Documentation (Valve/Actuator vendor files, FAT documentation, Instrument data sheets) |  | Vendor manuals, valve/actuator FAT reports, instrument datasheets, IOM manuals, calibration certificates, wiring diagrams, communication protocol sheets

## Chklist n Specs - Assoc Infra
Scope Of Work Checklist & Specifications - Associated Infrastructures
Date | 2025-12-15
|  | SYSTEM / SUBSYSTEM |  | WORK SCOPE SPECIFICATION
A | Utilities Design
| 1.1 | Process Design Package (P&IDs, mass/energy balances) |  | P&IDs & Process Design Basis to be produced; design pressure & MAWP per contract; process rating: design flow / composition per EPC SOW; PFD/P&ID with tag numbers, instrument loops, reliefs, pigging interfaces.
B | Procurement & Fabrication
| 1 | Procurement
|  | 1.1 | Process Skids & Packages | Modular skid units; design pressure typically 30 barg; corrosion allowance 3 mm; materials CS/SS316/Alloy depending on service
|  | 1.2 | Linepipe & Process Piping | Carbon steel ASTM A106 Gr.B; SS316L for corrosive service; thickness per ASME B31.3; flanges B16.5/16.47; gaskets B16.20/21
|  | 1.3 | Valves | Ball/gate/globe valves; Class 300–900; pressure tested per API 598; pipeline valves per API 6D
|  | 1.4 | Pressure Vessels | Vessels to MAWP 30 barg unless otherwise specified; CA 3 mm; MDMT -29°C
|  | 1.5 | Heat Exchangers | Shell & Tube; TEMA Class C; tube material ASTM A179; design temp 150°C
|  | 1.6 | Mechanical Equipment | Pumps API 610; mechanical seals API 682; vibration limits per ISO 10816
|  | 1.7 | Electrical Equipment | 11 kV/415 V switchgear; LV/MV cables IEC 60502; UPS per IEC 62040
|  | 1.8 | Instrumentation | 4–20 mA/HART transmitters; SIL-rated logic per IEC 61511; RTU/PLC per SCADA spec
|  | 1.9 | Structural Steel | ASTM A36/A992; hot-dip galvanized per ASTM A123
|  | 1.91 | Tanks (Atmospheric) | API 650 tanks; hydrotest per API 650 7.3; internal coating ISO 12944 C4/C5
|  | 1.92 | Fire Protection Systems | Hydrants, deluge, foam skid UL/FM certified
| 2 | Fabrication
|  | 2.1 | Structural Steel Fabrication | Cutting, welding per AWS D1.1; galvanizing per ASTM A123; coating ISO 12944 C4/C5
|  | 2.2 | Skid Fabrication | Base frames from ASTM A36; levelness ±3 mm; lifting lugs load-tested 1.25×
|  | 2.3 | Piping Prefabrication | Spool fabrication; welds RT/UT per ASME V; hydrotest 1.5 × design pressure
|  | 2.4 | Pressure Vessel Fabrication | Fabrication to ASME VIII; PWHT as applicable; nameplates per UG-119
|  | 2.5 | Electrical Panel Assembly | Assembly in clean workshop; functional FAT; cable glands per IECEx
|  | 2.6 | Instrument Tubing & Racks | SS316 tubing ASTM A269; bending radius ≥ 3D; supports at ≤1.5 m
|  | 2.7 | Coating & Surface Prep | Blast to SA2.5; DFT per paint system (typically 250–350 μm)
C | Mechanical Works
| 1.1 | Erection and alignment of modular process skids |  | i) Skid baseplates leveled to ±2 mm across full length. ii) Anchor bolts ASTM F1554 Gr. 55; torque tightening to ±10% of required preload. iii) Rotating equipment alignment tolerance: 0.05–0.10 mm offset, 0.1 mm/m angular. iv) Lifting lugs certified to 2.0 × skid weight
| 1.2 | Installation of vessels, columns, heat exchangers, compressors, and pumps |  | i) Pressure vessels per ASME VIII Div.1; design pressure 30 barg, corrosion allowance 3 mm. ii) Heat exchanger design temperature 150°C; tubes ASTM A179; TEMA Class C. iii) Compressors: discharge pressure 20–40 barg, surge margin ≥ 15%. iv) Pumps: API 610; minimum NPSH margin 1 m above vendor requirement.
| 1.3 | Interconnecting piping (carbon, stainless, alloy steel) |  | i) Process piping ASME B31.3; carbon steel ASTM A106 Gr.B; stainless steel SS316L. ii) Minimum corrosion allowance 3 mm for wet gas service. iii) Wall thickness per ASME B36.10; flanges ASME B16.5 Class 300/600. iv) PWHT required for carbon steel > 19 mm WT
| 1.4 | Hook-up of process and utility lines |  | i) Storage tanks per API 650; hydrotest at 1.25 × design pressure. ii) Utility lines design pressure 5–10 barg, temperature 0–80°C. iii) Grounding per NFPA 780; bonding resistance ≤ 1 Ω. iv) Tie-in spools fabricated to ±3 mm dimensional tolerance.
| 1.5 | Firefighting, water, and HVAC systems |  | i) Firewater pumps NFPA 20; minimum head 120 m, flow 1500–2500 m³/hr. ii) HVAC design: indoor temperature 24–26°C, RH 50–60%; insulation per ISO 12241. iii) Firewater ring main: NPS 10–14", design pressure 10–12 barg. iv) Carbon steel piping ASTM A106 Gr.B; corrosion allowance 3 mm.
| 1.6 | Flare system installation and tie-in |  | i) Flare KO drum per API 521; liquid holdup capacity ≥ 15 minutes. ii) Flare stack height 65–85 m (dispersion modeling dependent). iii) Pilot gas pressure 2–3 barg; pilot reliability > 99%. iv) Pig launcher/receiver: design pressure 50 barg; closure ASME VIII certified.
D | Electrical & Instrumentation
| 1.1 | Plant power distribution |  | i) Primary distribution voltage: 11 kV; secondary LV distribution: 415 V, 3-phase, 50 Hz. ii) Switchgear short-circuit rating: 31.5 kA for 1 sec (IEC 62271). iii) Transformers: ONAN-type; 2 × 2.5 MVA units; impedance 6%. iv) Cables: XLPE per IEC 60502-1; minimum size 4-core 70–150 mm² depending on load. v) Power factor correction to 0.95 lagging.
| 1.2 | Substation and E-house installation |  | i) E-House HVAC sized for 35–45 W/m³ heat load. ii) Electrical rooms classified Zone 1/2 per IEC 60079-10-1 (hazardous area). iii) Minimum fire rating: 2 hours (UL 263 / NFPA 251). iv) Earthing grid resistance ≤ 1 Ω; conductor size 70 mm² Cu (IEEE 80). v) Cable trays NEMA VE-1; minimum loading 150 kg/m.
| 1.3 | Cabling and grounding systems |  | i) LV cables: XLPE insulated, min. 3.5-core 35–95 mm²; derating per IEC 60287. ii) Lighting: average lux levels — 100 lux (general), 300 lux (control rooms). iii) Pole lights IP66, corrosion-resistant, mounting height 6–9 m. iv) Earthing: GI/Cu electrode depth 3 m; step & touch potentials per IEEE 80. v) Ex-rated lighting in classified areas certified to IECEx.
| 1.4 | Control system, PLC/DCS installation and testing |  | i) PLC/DCS input/output capacity: 20% spare I/O minimum. ii) Control panel ingress protection IP54 (indoor), IP66 (outdoor). iii) Communication: fibre optic duplex, single-mode G.652D, min. 2 cores per link. iv) Controller scan time ≤ 10 ms; network redundancy via ring topology. v) FAT/SAT performed per IEC 61499 & vendor requirements.
| 1.5 | Fire and gas detection, emergency shutdown systems (ESD) |  | i) Gas detectors: catalytic/IR type, detection range 0–100% LEL, accuracy ± 2%. ii) Flame detectors: UV/IR with 3–5 sec response time. iii) Deluge system per NFPA 15; hydrants UL 246; firewater pressure 8–10 barg. iv) ESD pushbuttons: SIL 2/3 rated per IEC 61508, fail-safe design. v) F&G communication via redundant Modbus TCP or fibre optic loop.
| 1.6 | Lighting systems |  | i) Lighting: average lux levels — 100 lux (general), 300 lux (control rooms). ii) Pole lights IP66, corrosion-resistant, mounting height 6–9 m.
|  | 1.6.1 | Plant Area Lighting | Required for the; Process modules, Pipe racks, Compressor area, Flare area, Tank farm & Utilities i) LED floodlights (100–200 W; IEC 60598) ii) Zone 1/2 luminaires (Ex d IIA/IIB; 80–100 W; IEC 60079-1) iii) Tank farm lighting (Pole-mounted; 150 W)
|  | 1.6.2 | Street Lighting | Required for the; Internal access roads, Vehicle circulation routes & Fire access lanes i) Road LED luminaires (60–120 W; IEC 60598) ii) Pole height (6–10 m; IEC 60364) iii) Lux requirement on road (5–20 lux; ASHRAE / IEC 12464
|  | 1.6.3 | Fence Lighting / Perimeter Security Lighting | Required for; All GPP perimeter fencing, CCTV integration & intrusion detection i) LED perimeter lights (50-80 W) ii) 25–35 m spacing between the lights iii) Integration with CCTV (Infrared-compatible; IEC 62676)
|  | 1.6.4 | Security Lighting | Required for the; Guard posts, Control room perimeter & Entry gates i) LED perimeter lights (50-80 W) ii) 25–35 m spacing between the lights iii) Integration with CCTV (Infrared-compatible; IEC 62676)
|  | 1.6.5 | Emergency & Hazard Lighting | Required for the; Escape routes, Egress doors & Muster points i) Emergency exit luminaires (3-hour battery backup; IEC 60598-2-22) ii) Hazard beacons (Red/amber LED; OSHA) iii) Muster point lighting (20 lux; IEC 12464)
E | Telecommunication
| 1.1 | Fibre backbone & ODFs |  | Single-mode fibre ITU-T G.652D (min 24/48-core); burial 0.8–1.0 m; ODF patch panels SC/APC; fusion splicing; OTDR baseline.
| 1.2 | SCADA / RTU links |  | Duplex FO links, Ethernet 1 Gbps; protocol Modbus TCP / DNP3; redundant ring topology; latency <50 ms, packet loss <1%.
| 1.3 | CCTV / Access control |  | CCTV IP 1080p min; ONVIF compatible; NVR 30 days retention; access control per IEC 60839.
F | Utilities and Ancillary Systems
| 1.1 | Instrument air, nitrogen, potable and service water, and fuel gas systems |  | i) Instrument Air System: Air quality per ISO 8573-1 Class 2 (Particles ≤ 1 µm; Dew point ≤ −40°C; Oil ≤ 0.1 mg/m³); Compressor discharge pressure 7–8 barg; dryer outlet dew point −40°C; Air receiver capacity 1.5–2.0 m³ per 1000 Nm³/hr air load. ii) Nitrogen System: Nitrogen purity ≥ 95–99%; delivery pressure 8–10 barg; Vaporizer/receiver materials SS tubes per ASTM A789. iii) Potable Water: Treated per WHO drinking water standards, free chlorine residual 0.2–0.5 mg/L. iv) Service Water: Flow capacity 20–40 m³/hr, design pressure 6–8 barg. v) Fuel Gas: Supply pressure 8–12 barg; filtration via 5 µm coalescer; dew point control per EPC SOW requirements.
| 1.2 | Sewerage, drainage, and oily water systems |  | i) Sewer System: PVC/HDPE piping per ASME A112; slope 1–2%; Septic and lift stations sized for peak factor 3.0. ii) Oily Water System: API 421 separator sizing (Minimum retention time 30 minutes; Oil droplet separation ≥ 150 microns); Underground drainage: concrete Class 30 MPa, covers rated 25–40 tons.
| 1.3 | Flare knock-out drums and stacks |  | i) KO drum per API 521, with: Liquid retention time 20–30 minutes; Design pressure 3–5 barg; corrosion allowance 3 mm; Vessel materials SA 516 Gr. 70. ii) Flare Stack: Height 45–65 m based on dispersion modeling & radiation limits (< 6.3 kW/m² at fence line); Pilots per API 537, auto-ignition at > 1200°C; Flare tip sized for turn-down ratio 10:1.
| 1.4 | Cathodic protection systems for buried facilities |  | CP system per NACE SP0169 with: i) Pipe-to-soil protection potential −0.85V to −1.2V (Cu/CuSO₄). ii) Anodes: high-purity magnesium/sacrificial type per ASTM B843, mass 17–32 kg per unit depending on soil resistivity. iii) Test posts per ASTM G97, spacing 100–300 m. iv) TR units with output 50–100 A @ 50 V for impressed current systems.
| 1.5 | Communication systems (CCTV, telecoms, access control)
G | Testing, Pre-commissioning, and Commissioning
| 1.1 | Mechanical completion checks and punch listing |  | i) Mechanical completion shall achieve 100% system walkdown; punch items categorized A/B/C. ii) All piping checks per ASME B31.3, alignment tolerances within ±1 mm for flanges. iii) Verification of torque values within ±10% of vendor recommended. iv) Completion dossiers compiled per ISO format with checklists ≥ 95% completed prior to pre-commissioning.
| 1.2 | Pressure testing, flushing, and leak checks |  | i) Hydrotest: Test pressure 1.5 × design pressure; Hold time 2 hours minimum; pressure decay < 5%; Water quality: chloride content < 50 ppm. ii) Leak Testing: Pneumatic testing at 1.1 × design pressure, nitrogen used; safety exclusion radius enforced. iii) Flushing: Flow velocity ≥ 2.5 m/s for piping; ≥ 3.0 m/s for firewater lines; Cleanliness target: < 100 ppm suspended solids; strainers inspected after flushing.
| 1.3 | Loop checks and calibration of instruments |  | i) Loop checks per ISA 5.1, ensuring correct signal 4–20 mA or HART communication. ii) Instrument calibration to ±0.5% of span or per datasheet, whichever is tighter. iii) Pressure transmitters calibrated up to 1.1 × max operating pressure; temperature sensors checked at 3 points (low, mid, high). iv) Full logic verification: SIS trip at 90–95% of design safety limit.
| 1.4 | Cold and hot commissioning |  | i) Cold commissioning checks include: Motor solo runs ≥ 2 hours, vibration < 4.5 mm/s rms; Control valve stroke testing (open/close time < 3 seconds for ESD service). ii) Hot commissioning: Ramps to 100% design load with performance stabilization ≥ 4 hours; Temperature rise of rotating machines ≤ 70°C winding temperature; Process units tested at normal operating pressure ±10%.
| 1.5 | Performance guarantee test runs |  | i) Gas throughput verified to within ±2% of design nameplate capacity. ii) Fuel gas consumption within ±5% of design guarantee. iii) NGL/LPG recovery efficiency ≥ design recovery (e.g., Propane ≥ 85%, Butane ≥ 95%). iv) Compressor performance per ASME PTC 10, heat exchangers per ASME PTC 12.1. v) Duration of test run 72 hours continuous, no major process upsets allowed.
| 1.6 | Operator training and documentation handover |  | i) Training curriculum per ISA Training Guidelines; minimum 3–5 days for operators & technicians. ii) Handover documentation includes: O&M manuals per ISO/IEC 26514; As-built drawings per ISO 128; Commissioning dossiers per EPC format iii) Closeout packages must include all ITPs, FAT/SAT reports, calibration certificates, pressure test packages. iv) Handover target: 100% system turnover packages approved before RFSU (Ready for Start-Up).
H | HSE, Documentation & QA/QC
| 1.1 | HSE Management System |  | Implement ISO 45001-aligned HSE plan; PTW, JSA/JHA, daily toolbox talks; site HSE induction for all staff.
| 1.2 | HAZOP and safety reviews |  | i) HAZOP studies executed per IEC 61882, covering: All major process systems (gas inlet, dehydration, stabilization, NGL recovery, utilities); Each node requires full guide word analysis (NO/MORE/LESS/REVERSE/OTHER THAN); Action close-out target: 100% closure of Category A, ≥ 95% closure of B, before commissioning. ii) SIL determination and validation per IEC 61508/61511: ESD valves typically SIL 2, high-integrity loops SIL 3; Proof test interval: 1 year for SIL 2, 6 months for SIL 3. iii) Pre-startup safety review (PSSR): Minimum 60 checklist items covering process, mechanical, electrical, instrumentation, HSE; Must achieve 100% completion prior to gas-in.
| 1.3 | Fire & Emergency |  | Firewater per NFPA 20/13; hydrants UL/FM; flare radiation criteria per API 521; emergency response & muster plan.
| 1.4 | Preparation of operating manuals, as-built drawings, and maintenance manuals |  | i) As-built drawings developed in ISO 128 format with 100% redline incorporation; dimensions to ±2 mm accuracy for piping and ±5 mm for structural. ii) O&M manuals compiled per ISO 14224, including failure mode data, maintenance intervals, reliability data. iii) Final documentation package must include: P&IDs, GA drawings, cable schedules, cause & effect charts; Vendor manuals (all tagged equipment); Material certificates (EN 10204 3.1); Calibration certificates (traceable to ISO 17025) iv) Submission schedule: Draft (60%) → Intermediate (90%) → Final (100%) before commissioning. v) Digital deliverables in PDF + native format (DWG, Excel).
| 1.5 | Inspection Test Plans (ITP), QA/QC reports, and equipment datasheets |  | i) ITPs shall comply with ISO 9001 Quality Management requirements, incorporating: Hold points, Witness points, Review points; Minimum 3 QC checkpoints per piping weld ii) Welding procedures qualified per ASME IX; acceptance criteria per ASME V, with RT/UT acceptance level ≤ 2% defect rate (per project requirement). iii) NDT requirements: 100% radiography for critical service; 10–25% random RT for utility service; Liquid penetrant or magnetic particle 100% on stainless & alloy welds iv) Material traceability to EN 10204 3.1/3.2 for all pressure components. v) Equipment datasheets follow EPC standard template; design data must match vendor final approved drawings 100%.